## Datasheet (hidden)
DC Input | 1MWD3-V620 |  | 2MWD3-V620 |  | 3MWD3-V620 | [5 empty] | DC Input | 1MWD3-V620 |  | DC Input | 2MWD3-V620 |  | DC Input | 3MWD3-V620
| 1258WD3-HV620 |  | 2517WD3-HV620 |  | 3775WD3-HV620 | [6 empty] | 1258WD3-HV620 |  |  | 2517WD3-HV620 |  |  | 3775WD3-HV620
| min | max | min | max | min | max | [5 empty] | min | max |  | min | max |  | min | max
MPP Voltage range for PV [Vdc] | 887 | 1500 | 887 | 1500 | 887 | 1500 |  |  |  |  | MPP Voltage range for PV [Vdc] | 887 | 1500 | MPP Voltage range for PV [Vdc] | 887 | 1500 | MPP Voltage range for PV [Vdc] | 887 | 1500
SOC Voltage range for BPCS [Vdc] | [10 empty] | SOC Voltage range for BPCS [Vdc] |  |  | SOC Voltage range for BPCS [Vdc] |  |  | SOC Voltage range for BPCS [Vdc]
MPP Voltage range @ full power [Vdc] (1) | 887 | 1250 | 887 | 1250 | 887 | 1250 |  |  |  |  | MPP Voltage range @ full power [Vdc] (1) | 887 | 1250 | MPP Voltage range @ full power [Vdc] (1) | 887 | 1250 | MPP Voltage range @ full power [Vdc] (1) | 887 | 1250
SOC Voltage range @ full power [Vdc] (1) | [10 empty] | SOC Voltage range @ full power [Vdc] (1) |  |  | SOC Voltage range @ full power [Vdc] (1) |  |  | SOC Voltage range @ full power [Vdc] (1)
Max. DC voltage [Vdc] | 1500 |  | 1500 |  | 1500 | [5 empty] | Max. DC voltage [Vdc] | 1500 |  | Max. DC voltage [Vdc] | 1500 |  | Max. DC voltage [Vdc] | 1500
Rated input current at Vdc_min [A] @35ºC | 1600 |  | 3200 |  | 4800 | [5 empty] | Rated input current at Vdc_min [A] @35ºC | 1600 |  | Rated input current at Vdc_min [A] @35ºC | 3200 |  | Rated input current at Vdc_min [A] @35ºC | 4800
Rated input current at Vdc_min [A] @50ºC | 1440 |  | 2880 |  | 4320 | [5 empty] | Rated input current at Vdc_min [A] @50ºC | 1440 |  | Rated input current at Vdc_min [A] @50ºC | 2880 |  | Rated input current at Vdc_min [A] @50ºC | 4320
Max. Short circuit input current (2) | 10000 |  | 2x10000 |  | 3x10000 | [5 empty] | Max. Short circuit input current (2) | 10000 |  | Max. Short circuit input current (2) | 2x10000 |  | Max. Short circuit input current (2) | 3x10000
Number of MPPT | 1 |  | up to 2 |  | up to 3 | [5 empty] | Number of MPPT | 1 |  | Number of MPPT | up to 2 |  | Number of MPPT | up to 3
Switch type | DC load break switch | [9 empty] | Switch type | DC load break switch |  | Switch type | DC load break switch |  | Switch type | DC load break switch
DC overvoltage protection | SPD (type 2) | [9 empty] | DC overvoltage protection | SPD (type 2) |  | DC overvoltage protection | SPD (type 2) |  | DC overvoltage protection | SPD (type 2)
Number of DC Inputs | up to 12 |  | up to 24 |  | Up to 36 | [5 empty] | Number of DC Inputs | up to 12 |  | Number of DC Inputs | up to 24 |  | Number of DC Inputs | Up to 36
DC input protection (3) | Fuses | [9 empty] | DC input protection (3) | Fuses |  | DC input protection (3) | Fuses |  | DC input protection (3) | Fuses
Integrated DC monitoring | Optional | [9 empty] | Integrated DC monitoring | Optional |  | Integrated DC monitoring | Optional |  | Integrated DC monitoring | Optional
AC Output | [10 empty] | AC Output |  |  | AC Output |  |  | AC Output
Nominal AC voltage | 620 | [9 empty] | Nominal AC voltage | 620 |  | Nominal AC voltage | 620 |  | Nominal AC voltage | 620
Max. AC voltage range (4) | 90%-110% | [9 empty] | Max. AC voltage range (4) | 90%-110% |  | Max. AC voltage range (4) | 90%-110% |  | Max. AC voltage range (4) | 90%-110%
Frequency, f [Hz] | 50-60 | [9 empty] | Frequency, f [Hz] | 50-60 |  | Frequency, f [Hz] | 50-60 |  | Frequency, f [Hz] | 50-60
Frequency operation range [Hz] | f ±3Hz | [9 empty] | Frequency operation range [Hz] | f ±3Hz |  | Frequency operation range [Hz] | f ±3Hz |  | Frequency operation range [Hz] | f ±3Hz
Rated apparent AC power [kVA] @95ºF/35ºC up to 950Vdc (5) | 1455 |  | 2911 |  | 4367 |  | 35 | 950 | 1.1162 | 1.15 | Rated apparent AC power [kVA] @95ºF/35ºC up to 950Vdc (5) | 1455 |  | Rated apparent AC power [kVA] @95ºF/35ºC up to 950Vdc (5) | 2911 |  | Rated apparent AC power [kVA] @95ºF/35ºC up to 950Vdc (5) | 4367
Rated apparent AC power [kVA] @95ºF/35ºC up to 1250Vdc (5) | 1266 |  | 2532 |  | 3798 |  | 35 | 1250 | 1.1162 | 1 | Rated apparent AC power [kVA] @95ºF/35ºC up to 1250Vdc (5) | 1266 |  | Rated apparent AC power [kVA] @95ºF/35ºC up to 1250Vdc (5) | 2532 |  | Rated apparent AC power [kVA] @95ºF/35ºC up to 1250Vdc (5) | 3798
Rated apparent AC power [kVA] @122ºF/50ºC up to 950Vdc (5) | 1304 |  | 2608 |  | 3913 |  | 50 | 950 | 1 | 1.15 | Rated apparent AC power [kVA] @122ºF/50ºC up to 950Vdc (5) | 1304 |  | Rated apparent AC power [kVA] @122ºF/50ºC up to 950Vdc (5) | 2608 |  | Rated apparent AC power [kVA] @122ºF/50ºC up to 950Vdc (5) | 3913
Rated apparent AC power [kVA] @122ºF/50ºC up to 1250Vdc (5) | 1134 |  | 2268 |  | 3402 |  | 50 | 1250 | 1 | 1 | Rated apparent AC power [kVA] @122ºF/50ºC up to 1250Vdc (5) | 1134 |  | Rated apparent AC power [kVA] @122ºF/50ºC up to 1250Vdc (5) | 2268 |  | Rated apparent AC power [kVA] @122ºF/50ºC up to 1250Vdc (5) | 3402
Rated AC power. Pmax [kW] @ 122ºF/50ºC up to 1250Vdc (5) | 1447 |  | 2894 |  | 4342 |  | 35 | 950 | 1.1162 | 1.15 | Rated AC power. Pmax [kW] @ 122ºF/50ºC up to 1250Vdc (5) | 1447 |  | Rated AC power. Pmax [kW] @ 122ºF/50ºC up to 1250Vdc (5) | 2894 |  | Rated AC power. Pmax [kW] @ 122ºF/50ºC up to 1250Vdc (5) | 4342
Rated AC power. Pmax [kW] @ 122ºF/50ºC up to 1250Vdc (5) | 1258 |  | 2517 |  | 3775 |  | 35 | 1250 | 1.1162 | 1 | Rated AC power. Pmax [kW] @ 122ºF/50ºC up to 1250Vdc (5) | 1258 |  | Rated AC power. Pmax [kW] @ 122ºF/50ºC up to 1250Vdc (5) | 2517 |  | Rated AC power. Pmax [kW] @ 122ºF/50ºC up to 1250Vdc (5) | 3775
Total Current Demand Distortion (TDD) | <3% | [9 empty] | Total Current Demand Distortion (TDD) | <3% |  | Total Current Demand Distortion (TDD) | <3% |  | Total Current Demand Distortion (TDD) | <3%
Power factor | Adjustable | [9 empty] | Power factor | Adjustable |  | Power factor | Adjustable |  | Power factor | Adjustable
AC Cabinet | Integrated | [9 empty] | AC Cabinet | Integrated |  | AC Cabinet | Integrated |  | AC Cabinet | Integrated
Switch type | AC circuit breaker | [9 empty] | Switch type | AC circuit breaker |  | Switch type | AC circuit breaker |  | Switch type | AC circuit breaker
Number of handling switches | 1 |  | 2 |  | 3 | [5 empty] | Number of handling switches | 1 |  | Number of handling switches | 2 |  | Number of handling switches | 3
AC overvoltage protection | SPD (type 2) | [9 empty] | AC overvoltage protection | SPD (type 2) |  | AC overvoltage protection | SPD (type 2) |  | AC overvoltage protection | SPD (type 2)
Efficiency | [10 empty] | Efficiency |  |  | Efficiency |  |  | Efficiency
Maximum Peak Efficiency (7) | >98.8% | [9 empty] | Maximum Peak Efficiency (7) | >98.8% |  | Maximum Peak Efficiency (7) | >98.8% |  | Maximum Peak Efficiency (7) | >98.8%
European Efficiency (7) | >98.5% | [9 empty] | European Efficiency (7) | >98.5% |  | European Efficiency (7) | >98.5% |  | European Efficiency (7) | >98.5%
CEC Efficiency (7) | >98.6% | [9 empty] | CEC Efficiency (7) | >98.6% |  | CEC Efficiency (7) | >98.6% |  | CEC Efficiency (7) | >98.6%
Self-consumption in standby [W] (8) | <250 |  | <400 |  | <550 | [5 empty] | Self-consumption in standby [W] (8) | <250 |  | Self-consumption in standby [W] (8) | <400 |  | Self-consumption in standby [W] (8) | <550
Self-consumption in operation [kW] | <4.5 |  | <7 |  | <10 | [5 empty] | Self-consumption in operation [kW] | <4.5 |  | Self-consumption in operation [kW] | <7 |  | Self-consumption in operation [kW] | <10
Average daily Self-consumption 12h. (European profile) [Kw] | <2 |  | <3 |  | <4 | [5 empty] | Average daily Self-consumption 12h. (European profile) [Kw] | <2 |  | Average daily Self-consumption 12h. (European profile) [Kw] | <3 |  | Average daily Self-consumption 12h. (European profile) [Kw] | <4
Average daily Self-consumption 12h. (CEC profile) [Kw] | <3 |  | <4 |  | <5 | [5 empty] | Average daily Self-consumption 12h. (CEC profile) [Kw] | <3 |  | Average daily Self-consumption 12h. (CEC profile) [Kw] | <4 |  | Average daily Self-consumption 12h. (CEC profile) [Kw] | <5
Notes | [10 empty] | Notes |  |  | Notes |  |  | Notes
(1) At 100% Uac_nom, full power according to Figure 10 and cos ϕ = 1 | [10 empty] | (1) At 100% Uac_nom, full power according to Figure 10 and cos ϕ = 1 |  |  | (1) At 100% Uac_nom, full power according to Figure 10 and cos ϕ = 1 |  |  | (1) At 100% Uac_nom, full power according to Figure 10 and cos ϕ = 1
(2) Higher values under request | [10 empty] | (2) Higher values under request |  |  | (2) Higher values under request |  |  | (2) Higher values under request
(3) Different DC fuse sizes are available. Optionals for BPCS | [10 empty] | (3) Different DC fuse sizes are available. Optionals for BPCS |  |  | (3) Different DC fuse sizes are available. Optionals for BPCS |  |  | (3) Different DC fuse sizes are available. Optionals for BPCS
(4) Other voltage configurations are possible under request | [10 empty] | (4) Other voltage configurations are possible under request |  |  | (4) Other voltage configurations are possible under request |  |  | (4) Other voltage configurations are possible under request
(5) At nominal AC voltage. | [10 empty] | (5) At nominal AC voltage. |  |  | (5) At nominal AC voltage. |  |  | (5) At nominal AC voltage.
(6) Self-consumption is not considered in the efficiency measurement considering the rated current when the Vdc=1250Vdc and the ambient temperature bellow 35 ºC | [10 empty] | (6) Self-consumption is not considered in the efficiency measurement considering the rated current when the Vdc=1250Vdc and the ambient temperature bellow 35 ºC |  |  | (6) Self-consumption is not considered in the efficiency measurement considering the rated current when the Vdc=1250Vdc and the ambient temperature bellow 35 ºC |  |  | (6) Self-consumption is not considered in the efficiency measurement considering the rated current when the Vdc=1250Vdc and the ambient temperature bellow 35 ºC
(7) The losses in standby and consumption of auxiliaries may vary depending on the model of transformer required by the customer | [10 empty] | (7) The losses in standby and consumption of auxiliaries may vary depending on the model of transformer required by the customer |  |  | (7) The losses in standby and consumption of auxiliaries may vary depending on the model of transformer required by the customer |  |  | (7) The losses in standby and consumption of auxiliaries may vary depending on the model of transformer required by the customer

## Capability
Inverter Voltage | 620 |  |  |  |  | P (W) | Q _Ii(VAr) | Vi_need | Q_Vdc (Var) | Q(Var) | P(kW) | Q(kVAr) | Q_Ii(kVAr) | Vdc_min (V) | S(kVA) | cos fi
Voltage operation pu | 1 |  |  | P_manual (kW), Q>0 | 3750 | 3750000 | 1868166.1256 | 666.4753 | 1825941.4535 | 1825941.4535 | 3750 | 1825.9415 | 1868.1661 | 963.0597 | 4170.9186 | 0.89908 | Capacitive
Line-Line Voltage (V) | 620 |  |  | P_manual (kW), Q<0 | 2846 | 2846000 | -2394824.3571 | 552.9314 | -48695324.7009 | -2394824.3571 | 2846 | -2394.8244 | -2394.8244 | 800.6918 | 3719.5295 | 0.76515 | Inductive
Nm: Number of modules | 3 |  |  |  |  | 0 | 4450198.7965 | 726.6707 | 2103413.87 | 2103413.87 | 0 | 2103.4139 | 4450.1988 | 1049.1391 | 2103.4139 | 0
f(Hz) | 50 | wg(Hz) | 314.1593 |  |  | 200113.8064 | 4445207.6612 | 726.5592 | 2102628.007 | 2102628.007 | 200.1138 | 2102.628 | 4445.2077 | 1048.9796 | 2112.1293 | 0.094745
Height (m) | 2700 |  |  |  |  | 401417.9232 | 4430077.3817 | 726.2209 | 2100251.5449 | 2100251.5449 | 401.4179 | 2100.2515 | 4430.0774 | 1048.4959 | 2138.2687 | 0.18773
Temperature Max (ºC) ( TM) | 33 | TM_H_corrected(ºC) | 44.25 |  |  | 602722.04 | 4404691.8164 | 725.653 | 2096284.0107 | 2096284.0107 | 602.722 | 2096.284 | 4404.6918 | 1047.6839 | 2181.2108 | 0.27632
Vdc_min (Tmax) | 951.5 | Vdc_min(sat) | 951.5 |  |  | 804026.1568 | 4368852.3825 | 724.8506 | 2090724.6609 | 2090724.6609 | 804.0262 | 2090.7247 | 4368.8524 | 1046.5363 | 2239.9972 | 0.35894
TM_derating | 104.5% |  |  |  |  | 1005330.2737 | 4322269.8694 | 723.8062 | 2083572.4525 | 2083572.4525 | 1005.3303 | 2083.5725 | 4322.2699 | 1045.0428 | 2313.431 | 0.43456
Vdc_min derating | 114.9% |  |  |  |  | 1206634.3905 | 4264552.1557 | 722.5101 | 2074826.0427 | 2074826.0427 | 1206.6344 | 2074.826 | 4264.5522 | 1043.1894 | 2400.1812 | 0.50273
Total derating@ TM | 120% |  |  |  |  | 1407938.5073 | 4195186.3692 | 720.9493 | 2064483.7872 | 2064483.7872 | 1407.9385 | 2064.4838 | 4195.1864 | 1040.9575 | 2498.8766 | 0.56343
Temperature Min (ºC) ( Tm) | -5 | Tm_H_corrected(ºC) | 6.25 |  |  | 1609242.6241 | 4113513.4394 | 719.1073 | 2052543.7388 | 2052543.7388 | 1609.2426 | 2052.5437 | 4113.5134 | 1038.3234 | 2608.179 | 0.617
Vdc_MPPT (Tmin) | 1130 | Vdc_max(sat) | 1130 |  |  | 1810546.7409 | 4018691.776 | 716.9627 | 2039003.6456 | 2039003.6456 | 1810.5467 | 2039.0036 | 4018.6918 | 1035.2567 | 2726.8325 | 0.66397
Tm_derating | 111.6% |  |  |  |  | 2011850.8577 | 3909644.7535 | 714.4885 | 2023860.9487 | 2023860.9487 | 2011.8509 | 2023.8609 | 3909.6448 | 1031.7186 | 2853.6918 | 0.705
Vdc_derating(V) | 106% |  |  |  |  | 2213154.9745 | 3784983.0588 | 711.6495 | 2007112.7798 | 2007112.7798 | 2213.155 | 2007.1128 | 3784.9831 | 1027.6588 | 2987.7344 | 0.74075
Total derating@ Tm | 118.3% |  |  |  |  | 2414459.0914 | 3642886.2141 | 708.3995 | 1988755.9587 | 1988755.9587 | 2414.4591 | 1988.756 | 3642.8862 | 1023.0113 | 3128.0606 | 0.77187
[6 empty] | 2615763.2082 | 3480914.2316 | 704.6767 | 1968786.99 | 1968786.99 | 2615.7632 | 1968.787 | 3480.9142 | 1017.6877 | 3273.8875 | 0.79898
Derating factor for TM | 118.3% |  |  |  |  | 2817067.325 | 3295691.8961 | 700.3952 | 1947202.0598 | 1947202.0598 | 2817.0673 | 1947.2021 | 3295.6919 | 1011.5652 | 3424.5385 | 0.82261
[6 empty] | 3018371.4418 | 3082341.6286 | 695.4309 | 1923997.0319 | 1923997.0319 | 3018.3714 | 1923.997 | 3082.3416 | 1004.4662 | 3579.4316 | 0.84325
Vi_max (V) | 665.3846 |  |  |  |  | 3219675.5586 | 2833365.4171 | 689.5924 | 1899167.4442 | 1899167.4442 | 3219.6756 | 1899.1674 | 2833.3654 | 996.1172 | 3738.0674 | 0.86132
Ii (A) | 1242.32 |  |  |  |  | 3270001.5878 | 2764251.7299 | 687.963 | 1892705.6555 | 1892705.6555 | 3270.0016 | 1892.7057 | 2764.2517 | 993.787 | 3778.2595 | 0.86548
S_max (VA) | 4026082.3363 | S_base (kVA) | 4026.0823 |  |  | 3320327.617 | 2691900.1824 | 686.253 | 1886141.9557 | 1886141.9557 | 3320.3276 | 1886.142 | 2691.9002 | 991.3418 | 3818.6525 | 0.8695
Prated (W) | 4002276.1282 | Prated (kW) | 4002.2761 |  |  | 3370653.6462 | 2615988.4094 | 684.4543 | 1879476.2654 | 1879476.2654 | 3370.6536 | 1879.4763 | 2615.9884 | 988.7696 | 3859.2405 | 0.8734
[6 empty] | 3420979.6754 | 2536130.3732 | 682.5569 | 1872708.5038 | 1872708.5038 | 3420.9797 | 1872.7085 | 2536.1304 | 986.0564 | 3900.0178 | 0.87717
GPTech Inverter | 1 |  |  |  |  | 3471305.7046 | 2451857.1272 | 680.5489 | 1865838.5888 | 1865838.5888 | 3471.3057 | 1865.8386 | 2451.8571 | 983.185 | 3940.9792 | 0.88082
Inverter output current (A) | 1250 |  |  |  |  | 3521631.7338 | 2362589.3542 | 678.4155 | 1858866.437 | 1858866.437 | 3521.6317 | 1858.8664 | 2362.5894 | 980.1341 | 3982.1193 | 0.88436
[6 empty] | 3571957.763 | 2267596.9202 | 676.1378 | 1851791.9637 | 1851791.9637 | 3571.9578 | 1851.792 | 2267.5969 | 976.8771 | 4023.4333 | 0.88779
Set Point Calculation Tool (@Tmax) |  | Vdc_limited? | 2 |  |  | 3622283.7922 | 2165937.0224 | 673.6917 | 1844615.0826 | 1844615.0826 | 3622.2838 | 1844.6151 | 2165.937 | 973.3792 | 4064.9163 | 0.89111
P | 2846 | 2846 |  |  |  | 3672609.8214 | 2056355.1823 | 671.0451 | 1837335.7063 | 1837335.7063 | 3672.6098 | 1837.3357 | 2056.3552 | 969.5944 | 4106.5637 | 0.89433
| Q_ind_lim | -2394.8244 |  |  |  | 3722935.8506 | 1937117.4488 | 668.1533 | 1829953.7462 | 1829953.7462 | 3722.9359 | 1829.9537 | 1937.1174 | 965.4592 | 4148.371 | 0.89745
| Q_cap_lim | 3266.8988 |  |  |  | 3773261.8798 | 1805704.329 | 664.9516 | 1822469.1119 | 1805704.329 | 3773.2619 | 1805.7043 | 1805.7043 | 960.8808 | 4183.0698 | 0.90203
Q | 0 | 0 |  |  |  | 3823587.909 | 1658194.6188 | 661.3394 | 1814881.712 | 1658194.6188 | 3823.5879 | 1658.1946 | 1658.1946 | 955.7153 | 4167.6653 | 0.91744
PF | 1 | Io(P,Q) (A) | 2650.224 |  |  | 3873913.9382 | 1487837.5848 | 657.1429 | 1807191.4536 | 1487837.5848 | 3873.9139 | 1487.8376 | 1487.8376 | 949.7143 | 4149.8036 | 0.93352
Vdc_min(V) | 889.3955 |  |  |  |  | 3924239.9674 | 1280924.1292 | 652.0096 | 1799398.2424 | 1280924.1292 | 3924.24 | 1280.9241 | 1280.9241 | 942.3737 | 4128.0051 | 0.95064
Vac_max(V) | 614.9619 |  |  |  |  | 3974565.9967 | 998459.0849 | 644.936 | 1791501.9828 | 998459.0849 | 3974.566 | 998.4591 | 998.4591 | 932.2585 | 4098.06 | 0.96987
[6 empty] | 4024892.0259 | 436037.2122 | 630.662 | 1783502.5778 | 436037.2122 | 4002.2761 | 436.0372 | 436.0372 | 911.8466 | 4025.9586 | 0.99412
[6 empty] | 3974565.9967 | -126384.6605 | 615.9618 | -48542860.0013 | -126384.6605 | 3974.566 | -126.3847 | -126.3847 | 890.8254 | 3976.5749 | 0.99949
[6 empty] | 3924239.9674 | -408849.7048 | 608.4693 | -48550756.2609 | -408849.7048 | 3924.24 | -408.8497 | -408.8497 | 880.1111 | 3945.4806 | 0.99462
[6 empty] | 3873913.9382 | -615763.1604 | 602.9217 | -48558549.4721 | -615763.1604 | 3873.9139 | -615.7632 | -615.7632 | 872.1781 | 3922.5468 | 0.9876
[6 empty] | 3823587.909 | -786120.1944 | 598.3157 | -48566239.7305 | -786120.1944 | 3823.5879 | -786.1202 | -786.1202 | 865.5914 | 3903.5637 | 0.97951
[6 empty] | 3773261.8798 | -933629.9046 | 594.2985 | -48573827.1304 | -933629.9046 | 3773.2619 | -933.6299 | -933.6299 | 859.8469 | 3887.0516 | 0.97073
[6 empty] | 3722935.8506 | -1065043.0244 | 590.6967 | -48581311.7647 | -1065043.0244 | 3722.9359 | -1065.043 | -1065.043 | 854.6963 | 3872.282 | 0.96143
[6 empty] | 3672609.8214 | -1184280.7579 | 587.4095 | -48588693.7248 | -1184280.7579 | 3672.6098 | -1184.2808 | -1184.2808 | 849.9956 | 3858.8319 | 0.95174
[6 empty] | 3622283.7922 | -1293862.598 | 584.3722 | -48595973.1011 | -1293862.598 | 3622.2838 | -1293.8626 | -1293.8626 | 845.6522 | 3846.4296 | 0.94173
[6 empty] | 3571957.763 | -1395522.4957 | 581.5403 | -48603149.9822 | -1395522.4957 | 3571.9578 | -1395.5225 | -1395.5225 | 841.6026 | 3834.8879 | 0.93144
[6 empty] | 3521631.7338 | -1490514.9298 | 578.8815 | -48610224.4555 | -1490514.9298 | 3521.6317 | -1490.5149 | -1490.5149 | 837.8006 | 3824.0718 | 0.92091
[6 empty] | 3471305.7046 | -1579782.7028 | 576.3719 | -48617196.6073 | -1579782.7028 | 3471.3057 | -1579.7827 | -1579.7827 | 834.2118 | 3813.8795 | 0.91018
[6 empty] | 3420979.6754 | -1664055.9488 | 573.9926 | -48624066.5223 | -1664055.9488 | 3420.9797 | -1664.0559 | -1664.0559 | 830.8094 | 3804.2324 | 0.89926
[6 empty] | 3370653.6462 | -1743913.9849 | 571.7288 | -48630834.2839 | -1743913.9849 | 3370.6536 | -1743.914 | -1743.914 | 827.5721 | 3795.0681 | 0.88817
[6 empty] | 3320327.617 | -1819825.758 | 569.5685 | -48637499.9742 | -1819825.758 | 3320.3276 | -1819.8258 | -1819.8258 | 824.4829 | 3786.3361 | 0.87692
[6 empty] | 3270001.5878 | -1892177.3055 | 567.5019 | -48644063.674 | -1892177.3055 | 3270.0016 | -1892.1773 | -1892.1773 | 821.5277 | 3777.9949 | 0.86554
[6 empty] | 3219675.5586 | -1961290.9927 | 565.5207 | -48650525.4627 | -1961290.9927 | 3219.6756 | -1961.291 | -1961.291 | 818.6946 | 3770.0097 | 0.85402
[6 empty] | 3018371.4418 | -2210267.2041 | 558.3254 | -48675355.0504 | -2210267.2041 | 3018.3714 | -2210.2672 | -2210.2672 | 808.4053 | 3741.1024 | 0.80681
[6 empty] | 2817067.325 | -2423617.4717 | 552.0851 | -48698560.0783 | -2423617.4717 | 2817.0673 | -2423.6175 | -2423.6175 | 799.4816 | 3716.1526 | 0.75806
[6 empty] | 2615763.2082 | -2608839.8072 | 546.6097 | -48720145.0085 | -2608839.8072 | 2615.7632 | -2608.8398 | -2608.8398 | 791.6518 | 3694.3555 | 0.70804
[6 empty] | 2414459.0914 | -2770811.7897 | 541.7763 | -48740113.9772 | -2770811.7897 | 2414.4591 | -2770.8118 | -2770.8118 | 784.74 | 3675.1885 | 0.65696
[6 empty] | 2213154.9745 | -2912908.6344 | 537.5001 | -48758470.7983 | -2912908.6344 | 2213.155 | -2912.9086 | -2912.9086 | 778.6252 | 3658.2908 | 0.60497
[6 empty] | 2011850.8577 | -3037570.3291 | 533.7205 | -48775218.9672 | -3037570.3291 | 2011.8509 | -3037.5703 | -3037.5703 | 773.2203 | 3643.4019 | 0.55219
[6 empty] | 1810546.7409 | -3146617.3516 | 530.3922 | -48790361.6641 | -3146617.3516 | 1810.5467 | -3146.6174 | -3146.6174 | 768.4608 | 3630.3278 | 0.49873
[6 empty] | 1609242.6241 | -3241439.015 | 527.481 | -48803901.7573 | -3241439.015 | 1609.2426 | -3241.439 | -3241.439 | 764.2978 | 3618.9209 | 0.44467
[6 empty] | 1407938.5073 | -3323111.9448 | 524.9605 | -48815841.8057 | -3323111.9448 | 1407.9385 | -3323.1119 | -3323.1119 | 760.6935 | 3609.0669 | 0.39011
[6 empty] | 1206634.3905 | -3392477.7313 | 522.8103 | -48826184.0612 | -3392477.7313 | 1206.6344 | -3392.4777 | -3392.4777 | 757.6187 | 3600.6766 | 0.33511
[6 empty] | 1005330.2737 | -3450195.4449 | 521.0144 | -48834930.471 | -3450195.4449 | 1005.3303 | -3450.1954 | -3450.1954 | 755.0506 | 3593.6802 | 0.27975
[6 empty] | 804026.1568 | -3496777.9581 | 519.5605 | -48842082.6793 | -3496777.9581 | 804.0262 | -3496.778 | -3496.778 | 752.9715 | 3588.0237 | 0.22409
[6 empty] | 602722.04 | -3532617.3919 | 518.4391 | -48847642.0292 | -3532617.3919 | 602.722 | -3532.6174 | -3532.6174 | 751.3679 | 3583.6657 | 0.16819
[6 empty] | 401417.9232 | -3558002.9573 | 517.6433 | -48851609.5634 | -3558002.9573 | 401.4179 | -3558.003 | -3558.003 | 750.2299 | 3580.5756 | 0.11211
[6 empty] | 200113.8064 | -3573133.2368 | 517.1684 | -48853986.0255 | -3573133.2368 | 200.1138 | -3573.1332 | -3573.1332 | 749.5508 | 3578.7325 | 0.055918
[6 empty] | -1190.3104 | -3578124.1956 | 517.0117 | -48854771.8607 | -3578124.1956 | -1.1903 | -3578.1242 | -3578.1242 | 749.3267 | 3578.1244 | -0.00033266
Note on D8: Autor: Vdc_Min for Ii calculation. Used to open the loop of Ii dependency of Vdc and Vdc dependency of Ii
Note on B22: Autor: P_max no se da con reactiva 0 a la salida, por lo que el PF a la salida no es 1. La potencia es algo mayor que la rated porque la tension en bornas del stack de potencia es tb algo mayor
Note on B25: IF YES = '1' / NO = '0'

## Curves Value
Warning. These data are manually generated.
Model | PV3WD3HV620 | Vdc_min | 954
|  | Vdc_max | 1130
Curve 1 |  | Curve 2 |  | Curve 3 |  | Curve 4 |  | Curve 5 |  | Curve 6 |  | Curve 7
Vac | T | Vac | T | Vac | T | Vac | T | Vac | T | Vac | T | Vac | T
620 | 33 | 620 | -5
Vdc | 951.5 | Vdc | 1130 | Vdc |  | Vdc |  | Vdc |  | Vdc |  | Vdc
P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q
0 | 2103.4139 | 0 | 4450.1988
200.1138 | 2102.628 | 200.1138 | 4445.2077
401.4179 | 2100.2515 | 401.4179 | 4430.0774
602.722 | 2096.284 | 602.722 | 4404.6918
804.0262 | 2090.7247 | 804.0262 | 4368.8524
1005.3303 | 2083.5725 | 1005.3303 | 4322.2699
1206.6344 | 2074.826 | 1206.6344 | 4264.5522
1407.9385 | 2064.4838 | 1407.9385 | 4195.1864
1609.2426 | 2052.5437 | 1609.2426 | 4113.5134
1810.5467 | 2039.0036 | 1810.5467 | 4018.6918
2011.8509 | 2023.8609 | 2011.8509 | 3909.6448
2213.155 | 2007.1128 | 2213.155 | 3784.9831
2414.4591 | 1988.756 | 2414.4591 | 3642.8862
2615.7632 | 1968.787 | 2615.7632 | 3480.9142
2817.0673 | 1947.2021 | 2817.0673 | 3295.6919
3018.3714 | 1923.997 | 3018.3714 | 3082.3416
3219.6756 | 1899.1674 | 3219.6756 | 2833.3654
3270.0016 | 1892.7057 | 3270.0016 | 2764.2517
3320.3276 | 1886.142 | 3320.3276 | 2691.9002
3370.6536 | 1879.4763 | 3370.6536 | 2615.9884
3420.9797 | 1872.7085 | 3420.9797 | 2536.1304
3471.3057 | 1865.8386 | 3471.3057 | 2451.8571
3521.6317 | 1858.8664 | 3521.6317 | 2362.5894
3571.9578 | 1851.792 | 3571.9578 | 2267.5969
3622.2838 | 1844.6151 | 3622.2838 | 2165.937
3672.6098 | 1837.3357 | 3672.6098 | 2056.3552
3722.9359 | 1829.9537 | 3722.9359 | 1937.1174
3773.2619 | 1805.7043 | 3773.2619 | 1805.7043
3823.5879 | 1658.1946 | 3823.5879 | 1658.1946
3873.9139 | 1487.8376 | 3873.9139 | 1487.8376
3924.24 | 1280.9241 | 3924.24 | 1280.9241
3974.566 | 998.4591 | 3974.566 | 998.4591
4002.2761 | 436.0372 | 4002.2761 | 436.0372
3974.566 | -126.3847 | 3974.566 | -126.3847
3924.24 | -408.8497 | 3924.24 | -408.8497
3873.9139 | -615.7632 | 3873.9139 | -615.7632
3823.5879 | -786.1202 | 3823.5879 | -786.1202
3773.2619 | -933.6299 | 3773.2619 | -933.6299
3722.9359 | -1065.043 | 3722.9359 | -1065.043
3672.6098 | -1184.2808 | 3672.6098 | -1184.2808
3622.2838 | -1293.8626 | 3622.2838 | -1293.8626
3571.9578 | -1395.5225 | 3571.9578 | -1395.5225
3521.6317 | -1490.5149 | 3521.6317 | -1490.5149
3471.3057 | -1579.7827 | 3471.3057 | -1579.7827
3420.9797 | -1664.0559 | 3420.9797 | -1664.0559
3370.6536 | -1743.914 | 3370.6536 | -1743.914
3320.3276 | -1819.8258 | 3320.3276 | -1819.8258
3270.0016 | -1892.1773 | 3270.0016 | -1892.1773
3219.6756 | -1961.291 | 3219.6756 | -1961.291
3018.3714 | -2210.2672 | 3018.3714 | -2210.2672
2817.0673 | -2423.6175 | 2817.0673 | -2423.6175
2615.7632 | -2608.8398 | 2615.7632 | -2608.8398
2414.4591 | -2770.8118 | 2414.4591 | -2770.8118
2213.155 | -2912.9086 | 2213.155 | -2912.9086
2011.8509 | -3037.5703 | 2011.8509 | -3037.5703
1810.5467 | -3146.6174 | 1810.5467 | -3146.6174
1609.2426 | -3241.439 | 1609.2426 | -3241.439
1407.9385 | -3323.1119 | 1407.9385 | -3323.1119
1206.6344 | -3392.4777 | 1206.6344 | -3392.4777
1005.3303 | -3450.1954 | 1005.3303 | -3450.1954
804.0262 | -3496.778 | 804.0262 | -3496.778
602.722 | -3532.6174 | 602.722 | -3532.6174
401.4179 | -3558.003 | 401.4179 | -3558.003
200.1138 | -3573.1332 | 200.1138 | -3573.1332
-1.1903 | -3578.1242 | -1.1903 | -3578.1242

## Ii_Derating
Temperature derating
| Ii(T) (A) |  |  | Ii(T)(%In)
Temp(ºC) | 35 | 50 | 60 | -20 | 35 | 50 | 60
Ii(A)/Ii(%) | 1172 | 1050 | 756 | 111.6% | 111.6% | 100% | 72%
Ii DC Voltage derating
DC Voltage(V) | 500 | 950 | 1250 | 1350 | 1500 | 1500
WD3V | 115% | 115% | 100% | 45% | 5% | 0%
Altitude derating
Altitude | H<1000 | 1000<H<2000 | 2000<H<4000
Operation temperature derating value (ºC/1000m) | 0 | 6 | 7.5
WD3 voltage dependecy on altitude
Altitude(m) | 0 | 2000 | 3000 | 4000
Max DC (Altirude derating) (V) | 1500 | 1500 | 1320 | 1170
Max AC(Altitude derating) (V) | 690 | 690 | 607.2 | 538.2
Total derating curves example
Warning: The maximum output current of the inverter will also depend on the AC/DC
| Pbase | 3382.6952
Vdc
|  |  | 1250 | 1200 | 1100 | 1000 | 950
| %Ii(T) | Temp | S(kVA) @ 1250V | S(kVA) @ 1200V | S(kVA) @ 1100V | S(kVA) @ 1000V | S(kVA) @ 950V
| 111.6% | -20 | 3775.7322 | 3871.3068 | 4062.4559 | 4253.605 | 4349.1796
| 111.6% | 35 | 3775.7322 | 3871.3068 | 4062.4559 | 4253.605 | 4349.1796
| 100% | 50 | 3382.6952 | 3468.3209 | 3639.5723 | 3810.8236 | 3896.4493
| 72% | 60 | 2435.5406 | 2497.191 | 2620.492 | 2743.793 | 2805.4435
Temp (H modified)
|  |  | 30 | 40 | 50
| %Ii(V) | Vdc | S(kVA) @ 30ºC | S(kVA) @ 40ºC | S(kVA) @ 50ºC
| 115.2% | 500 | 4349.1796 | 4198.2695 | 3896.4493
| 115.2% | 950 | 4349.1796 | 4198.2695 | 3896.4493
| 100% | 1250 | 3775.7322 | 3644.7199 | 3382.6952
| 45% | 1350 | 1699.0795 | 1640.1239 | 1522.2129
| 5% | 1500 | 188.7866 | 182.236 | 169.1348
Note on A4: Autor: Esta tabla tiene que estar siempre ordenada de menor a mayor(de A a Z)

## aux (hidden)
Ii_rated | 1050 | [5 empty] | Inverter voltages | Si
| 1.1567 | [5 empty] | 400 | No
440
480
530
| deltaT | 11.25 |  |  |  |  | 560
| Temperature | Rating | STEP1 | STEP2 | Delta T/1000m (ºC/1000m).1000< H <2000 | Delta T/1000m (ºC/1000m). H>2000m | 575
| -20 | 111.6% | 118.3% | 118.3% | 6 | 7.5 | 590
| -10 | 111.6% | 118.3% | 118.3% |  |  | 605
| 0 | 111.6% | 118.3% | 118.3% |  |  | 620
| 35 | 111.6% | 118.3% | 118.3% |  |  | 630
| 50 | 100% | 115% | 115% |  |  | 650
| 60 | 72% | 82.8% | 82.8% |  |  | 660
690
| Vdc | Rating
| 950 | 115% | Desactiva Vdc uprating poniendo este valor a 100%. Activarlo poniendolo a 115,2%
| 1250 | 100%
| 1350 | 45%
| 1500 | 5%
Li (H) | 0.00013
Co (F) | 0.0012
Lo (H) | 2.5e-05
k1 (wg) | 0.9846
k2 (wg) | 0.048574
k3 (wg) | 0.99704
k4 (wg) | 0.37699
| Ii | Io | Vdc | Vdc_min derating | Ii_lim
STEP1 | 1206.7125 | 1202.7043 | 894.8602 | 1.15 | 1242.32 | 1.1832
STEP2 | -29272.215 | 29358.832 | 939.3565 | 1.15
STEP3 | -29272.215 | 29358.832 | 939.3565
𝑄_(𝑜_𝑖𝑛𝑑)=𝑁𝑚·(−√(3/(𝑘_3^2 )·〖𝑉_𝑜〗^2·〖𝐼_𝑖〗^2−〖𝑃_𝑜〗^2 )+𝑘_4/𝑘_3 ·𝑉_𝑜^2 )
MIN IMUM BETWEEN
AND
MIN IMUM BETWEEN
𝑄_(𝑜_𝑐𝑎𝑝)=𝑁𝑚·(𝑘_4/𝑘_3 ·𝑉_𝑜^2+√(3/(𝑘_3^2 )·〖𝑉_𝑜〗^2·〖𝐼_𝑖〗^2−〖𝑃_𝑜〗^2 ))
AND
𝑄_(𝑜_𝑐𝑎𝑝)=𝑁𝑚·(−𝑘_1/𝑘_2 ·𝑉_𝑜^2+√((〖3·𝑉〗_𝑜^2·〖〖(1.43·𝑉𝑑𝑐〗^2+10)〗^2)/(𝑘_2^2 )−𝑃_𝑜^2 ))

## V_0,9pu_DIG (hidden)
Inverter Voltage | 620 |  |  |  |  | P (W) | Q _Ii(VAr) | Vi_need | Q_Vdc (Var) | Q(Var) | P(kW) | Q_Ii(kVAr) | Vdc_min (V) | Q(kVAr) | S(kVA) | cos fi
Voltage operation pu | 0.9 |  |  | P_manual (kW), Q>0 | 3750 | 3750000 | 353190.1419 | 570.1369 | 3688181.7607 | 353190.1419 | 3750 | 353.1901 | 825.2958 | 353.1901 | 3766.5957 | 0.99559 | Capacitive
Line-Line Voltage (V) | 558 |  |  | P_manual (kW), Q<0 | 2846 | 2846000 | -1872166.7985 | 501.9249 | -41688189.0035 | -1872166.7985 | 2846 | -1872.1668 | 727.7526 | -1872.1668 | 3406.5708 | 0.83544 | Inductive
Nm: Number of modules | 3 |  |  |  |  | 0 | 3965935.5677 | 664.4866 | 3996883.5938 | 3965935.5677 | 0 | 3965.9356 | 960.2159 | 3965.9356 | 3965.9356 | 0
f(Hz) | 50 | wg(Hz) | 314.1593 |  |  | 221434.5285 | 3959143.0342 | 664.3206 | 3995814.4298 | 3959143.0342 | 221.4345 | 3959.143 | 959.9784 | 3959.143 | 3965.3306 | 0.055843
Height (m) | 2700 |  |  |  |  | 442869.057 | 3938688.2259 | 663.8204 | 3992606.6385 | 3938688.2259 | 442.8691 | 3938.6882 | 959.2631 | 3938.6882 | 3963.5083 | 0.11174
Temperature Max (ºC) ( TM) | 33 | TM_H_corrected(ºC) | 44.25 |  |  | 664303.5855 | 3904335.0641 | 662.9795 | 3987259.3222 | 3904335.0641 | 664.3036 | 3904.3351 | 958.0606 | 3904.3351 | 3960.4459 | 0.16773
Vdc_min (Tmax) | 951.5 | Vdc_min(sat) | 951.5 |  |  | 885738.114 | 3855674.618 | 661.7865 | 3979770.9829 | 3855674.618 | 885.7381 | 3855.6746 | 956.3546 | 3855.6746 | 3956.104 | 0.22389
TM_derating | 104.5% |  |  |  |  | 1107172.6425 | 3792099.5986 | 660.2246 | 3970139.5206 | 3792099.5986 | 1107.1726 | 3792.0996 | 954.1211 | 3792.0996 | 3950.4241 | 0.28027
Vdc_min derating | 114.9% |  |  |  |  | 1328607.171 | 3712763.4031 | 658.2703 | 3958362.2305 | 3712763.4031 | 1328.6072 | 3712.7634 | 951.3265 | 3712.7634 | 3943.3246 | 0.33693
Total derating@ TM | 120% |  |  |  |  | 1550041.6995 | 3616516.7026 | 655.8916 | 3944435.7986 | 3616516.7026 | 1550.0417 | 3616.5167 | 947.925 | 3616.5167 | 3934.6947 | 0.39394
Temperature Min (ºC) ( Tm) | -5 | Tm_H_corrected(ºC) | 6.25 |  |  | 1771476.228 | 3501809.1226 | 653.0454 | 3928356.2977 | 3501809.1226 | 1771.4762 | 3501.8091 | 943.8549 | 3501.8091 | 3924.3847 | 0.4514
Vdc_max (Tmin) | 1130 | Vdc_max(sat) | 1130 |  |  | 1992910.7564 | 3366533.1739 | 649.6727 | 3910119.1813 | 3366533.1739 | 1992.9108 | 3366.5332 | 939.032 | 3366.5332 | 3912.1911 | 0.50941
Tm_derating | 111.6% |  |  |  |  | 2214345.2849 | 3207766.1999 | 645.692 | 3889719.2773 | 3207766.1999 | 2214.3453 | 3207.7662 | 933.3395 | 3207.7662 | 3897.8313 | 0.5681
Vdc_derating(V) | 106% |  |  |  |  | 2435779.8134 | 3021317.9897 | 640.9856 | 3867150.7809 | 3021317.9897 | 2435.7798 | 3021.318 | 926.6094 | 3021.318 | 3880.9001 | 0.62763
Total derating@ Tm | 118.3% |  |  |  |  | 2657214.3419 | 2800870.9734 | 635.376 | 3842407.2457 | 2800870.9734 | 2657.2143 | 2800.871 | 918.5877 | 2800.871 | 3860.7857 | 0.68826
[6 empty] | 2878648.8704 | 2536149.187 | 628.5737 | 3815481.5746 | 2536149.187 | 2878.6489 | 2536.1492 | 908.8604 | 2536.1492 | 3836.4922 | 0.75033
Derating factor for TM | 118.3% |  |  |  |  | 3100083.3989 | 2208294.568 | 620.0456 | 3786366.0099 | 2208294.568 | 3100.0834 | 2208.2946 | 896.6653 | 2208.2946 | 3806.19 | 0.81448
[6 empty] | 3321517.9274 | 1774263.0358 | 608.572 | 3755052.121 | 1774263.0358 | 3321.5179 | 1774.263 | 880.2579 | 1774.263 | 3765.6992 | 0.88205
Vi_max (V) | 658.3916 |  |  |  |  | 3542952.4559 | 1059884.8477 | 589.201 | 3721530.7927 | 1059884.8477 | 3542.9525 | 1059.8848 | 852.5574 | 1059.8848 | 3698.0898 | 0.95805
Ii (A) | 1242.32 |  |  |  |  | 3598311.088 | 675815.0413 | 578.5185 | 3712804.4137 | 675815.0413 | 3598.3111 | 675.815 | 837.2815 | 675.815 | 3661.225 | 0.98282
P_max (W) (kW) | 3623474.1026 | P_base (kW) | 3623.4741 |  |  | 3653669.7202 | 353190.1419 | 569.6101 | 3703939.2997 | 353190.1419 | 3653.6697 | 353.1901 | 824.5424 | 353.1901 | 3670.701 | 0.99536
Prated (W) | 3602048.5154 | Prated (kW) | 3602.0485 |  |  | 3709028.3523 | 353190.1419 | 569.9112 | 3694935.2874 | 353190.1419 | 3709.0284 | 353.1901 | 824.9731 | 353.1901 | 3725.8066 | 0.9955
[6 empty] | 3764386.9844 | 353190.1419 | 570.2168 | 3685792.2112 | 353190.1419 | 3764.387 | 353.1901 | 825.41 | 353.1901 | 3780.9196 | 0.99563
GPTech Inverter | 1 |  |  |  |  | 3819745.6165 | 353190.1419 | 570.5266 | 3676509.9023 | 353190.1419 | 3819.7456 | 353.1901 | 825.8531 | 353.1901 | 3836.0396 | 0.99575
Inverter output current (A) | 1250 |  |  |  |  | 3875104.2486 | 353190.1419 | 570.8409 | 3667088.1891 | 353190.1419 | 3875.1042 | 353.1901 | 826.3025 | 353.1901 | 3891.1664 | 0.99587
[6 empty] | 3930462.8808 | 353190.1419 | 571.1595 | 3657526.8972 | 353190.1419 | 3930.4629 | 353.1901 | 826.758 | 353.1901 | 3946.2998 | 0.99599
Set Point Calculation Tool (@Tmax) | [5 empty] | 3985821.5129 | 353190.1419 | 571.4824 | 3647825.8494 | 353190.1419 | 3985.8215 | 353.1901 | 827.2198 | 353.1901 | 4001.4393 | 0.9961
P | 2846 | 2846 |  |  |  | 4041180.145 | 353190.1419 | 571.8096 | 3637984.8655 | 353190.1419 | 4041.1801 | 353.1901 | 827.6878 | 353.1901 | 4056.5848 | 0.9962
| Q_ind_lim | -1872.1668 |  |  |  | 4096538.7771 | 353190.1419 | 572.1412 | 3628003.7622 | 353190.1419 | 4096.5388 | 353.1901 | 828.1619 | 353.1901 | 4111.736 | 0.9963
| Q_cap_lim | 2578.5471 |  |  |  | 4151897.4093 | 353190.1419 | 572.4771 | 3617882.3537 | 353190.1419 | 4151.8974 | 353.1901 | 828.6422 | 353.1901 | 4166.8928 | 0.9964
Q | 0 | 0 |  |  |  | 4207256.0414 | 353190.1419 | 572.8173 | 3607620.4509 | 353190.1419 | 4207.256 | 353.1901 | 829.1287 | 353.1901 | 4222.0548 | 0.99649
PF | 1 | Io(P,Q) (A) | 2944.6933 |  |  | 4262614.6735 | 353190.1419 | 573.1618 | 3597217.8618 | 353190.1419 | 4262.6147 | 353.1901 | 829.6213 | 353.1901 | 4277.2219 | 0.99658
Vdc_min(V) | 804.48 |  |  |  |  | 4317973.3056 | 353190.1419 | 573.5105 | 3586674.3915 | 353190.1419 | 4317.9733 | 353.1901 | 830.1201 | 353.1901 | 4332.3939 | 0.99667
Vac_max(V) | 555.5804 |  |  |  |  | 4373331.9378 | 353190.1419 | 573.8636 | 3575989.8421 | 353190.1419 | 4373.3319 | 353.1901 | 830.625 | 353.1901 | 4387.5706 | 0.99675
[6 empty] | 4428690.5699 | 353190.1419 | 574.221 | 3565164.0125 | 353190.1419 | 4428.6906 | 353.1901 | 831.136 | 353.1901 | 4442.7518 | 0.99684
[6 empty] | 4373331.9378 | 353190.1419 | 573.8636 | -41444589.8371 | 353190.1419 | 4373.3319 | 353.1901 | 830.625 | 353.1901 | 4387.5706 | 0.99675
[6 empty] | 4317973.3056 | 353190.1419 | 573.5105 | -41455274.3865 | 353190.1419 | 4317.9733 | 353.1901 | 830.1201 | 353.1901 | 4332.3939 | 0.99667
[6 empty] | 4262614.6735 | 353190.1419 | 573.1618 | -41465817.8568 | 353190.1419 | 4262.6147 | 353.1901 | 829.6213 | 353.1901 | 4277.2219 | 0.99658
[6 empty] | 4207256.0414 | 353190.1419 | 572.8173 | -41476220.4459 | 353190.1419 | 4207.256 | 353.1901 | 829.1287 | 353.1901 | 4222.0548 | 0.99649
[6 empty] | 4151897.4093 | 353190.1419 | 572.4771 | -41486482.3487 | 353190.1419 | 4151.8974 | 353.1901 | 828.6422 | 353.1901 | 4166.8928 | 0.9964
[6 empty] | 4096538.7771 | 353190.1419 | 572.1412 | -41496603.7572 | 353190.1419 | 4096.5388 | 353.1901 | 828.1619 | 353.1901 | 4111.736 | 0.9963
[6 empty] | 4041180.145 | 353190.1419 | 571.8096 | -41506584.8605 | 353190.1419 | 4041.1801 | 353.1901 | 827.6878 | 353.1901 | 4056.5848 | 0.9962
[6 empty] | 3985821.5129 | 353190.1419 | 571.4824 | -41516425.8444 | 353190.1419 | 3985.8215 | 353.1901 | 827.2198 | 353.1901 | 4001.4393 | 0.9961
[6 empty] | 3930462.8808 | 353190.1419 | 571.1595 | -41526126.8922 | 353190.1419 | 3930.4629 | 353.1901 | 826.758 | 353.1901 | 3946.2998 | 0.99599
[6 empty] | 3875104.2486 | 353190.1419 | 570.8409 | -41535688.1841 | 353190.1419 | 3875.1042 | 353.1901 | 826.3025 | 353.1901 | 3891.1664 | 0.99587
[6 empty] | 3819745.6165 | 353190.1419 | 570.5266 | -41545109.8973 | 353190.1419 | 3819.7456 | 353.1901 | 825.8531 | 353.1901 | 3836.0396 | 0.99575
[6 empty] | 3764386.9844 | 353190.1419 | 570.2168 | -41554392.2062 | 353190.1419 | 3764.387 | 353.1901 | 825.41 | 353.1901 | 3780.9196 | 0.99563
[6 empty] | 3709028.3523 | 353190.1419 | 569.9112 | -41563535.2824 | 353190.1419 | 3709.0284 | 353.1901 | 824.9731 | 353.1901 | 3725.8066 | 0.9955
[6 empty] | 3653669.7202 | 353190.1419 | 569.6101 | -41572539.2946 | 353190.1419 | 3653.6697 | 353.1901 | 824.5424 | 353.1901 | 3670.701 | 0.99536
[6 empty] | 3598311.088 | 30565.2425 | 560.1132 | -41581404.4087 | 30565.2425 | 3598.3111 | 30.5652 | 810.9619 | 30.5652 | 3598.4409 | 0.99996
[6 empty] | 3542952.4559 | -353504.5639 | 548.865 | -41590130.7877 | -353504.5639 | 3542.9525 | -353.5046 | 794.8769 | -353.5046 | 3560.5446 | 0.99506
[6 empty] | 3321517.9274 | -1067882.752 | 527.3051 | -41623652.116 | -1067882.752 | 3321.5179 | -1067.8828 | 764.0464 | -1067.8828 | 3488.9619 | 0.95201
[6 empty] | 3100083.3989 | -1501914.2842 | 513.7645 | -41654966.0049 | -1501914.2842 | 3100.0834 | -1501.9143 | 744.6832 | -1501.9143 | 3444.7443 | 0.89995
[6 empty] | 2878648.8704 | -1829768.9033 | 503.2948 | -41684081.5696 | -1829768.9033 | 2878.6489 | -1829.7689 | 729.7116 | -1829.7689 | 3410.9637 | 0.84394
[6 empty] | 2657214.3419 | -2094490.6896 | 494.6795 | -41711007.2406 | -2094490.6896 | 2657.2143 | -2094.4907 | 717.3917 | -2094.4907 | 3383.4419 | 0.78536
[6 empty] | 2435779.8134 | -2314937.706 | 487.389 | -41735750.7759 | -2314937.706 | 2435.7798 | -2314.9377 | 706.9662 | -2314.9377 | 3360.3512 | 0.72486
[6 empty] | 2214345.2849 | -2501385.9161 | 481.1366 | -41758319.2723 | -2501385.9161 | 2214.3453 | -2501.3859 | 698.0253 | -2501.3859 | 3340.697 | 0.66284
[6 empty] | 1992910.7564 | -2660152.8902 | 475.7477 | -41778719.1763 | -2660152.8902 | 1992.9108 | -2660.1529 | 690.3192 | -2660.1529 | 3323.8692 | 0.59958
[6 empty] | 1771476.228 | -2795428.8388 | 471.1075 | -41796956.2927 | -2795428.8388 | 1771.4762 | -2795.4288 | 683.6838 | -2795.4288 | 3309.4638 | 0.53528
[6 empty] | 1550041.6995 | -2910136.4188 | 467.1368 | -41813035.7936 | -2910136.4188 | 1550.0417 | -2910.1364 | 678.0056 | -2910.1364 | 3297.1993 | 0.47011
[6 empty] | 1328607.171 | -3006383.1193 | 463.7788 | -41826962.2255 | -3006383.1193 | 1328.6072 | -3006.3831 | 673.2037 | -3006.3831 | 3286.8734 | 0.40422
[6 empty] | 1107172.6425 | -3085719.3149 | 460.9925 | -41838739.5156 | -3085719.3149 | 1107.1726 | -3085.7193 | 669.2192 | -3085.7193 | 3278.3372 | 0.33772
[6 empty] | 885738.114 | -3149294.3342 | 458.7475 | -41848370.9778 | -3149294.3342 | 885.7381 | -3149.2943 | 666.0089 | -3149.2943 | 3271.4808 | 0.27075
[6 empty] | 664303.5855 | -3197954.7803 | 457.0217 | -41855859.3172 | -3197954.7803 | 664.3036 | -3197.9548 | 663.541 | -3197.9548 | 3266.2232 | 0.20339
[6 empty] | 442869.057 | -3232307.9421 | 455.7994 | -41861206.6335 | -3232307.9421 | 442.8691 | -3232.3079 | 661.7931 | -3232.3079 | 3262.5063 | 0.13575
[6 empty] | 221434.5285 | -3252762.7504 | 455.07 | -41864414.4248 | -3252762.7504 | 221.4345 | -3252.7628 | 660.7501 | -3252.7628 | 3260.2912 | 0.067919
[6 empty] | -5.2387e-10 | -3259555.284 | 454.8275 | -41865483.5888 | -3259555.284 | -5.2387e-13 | -3259.5553 | 660.4034 | -3259.5553 | 3259.5553 | -1.6072e-16
Note on B22: Autor: P_max no se da con reactiva 0 a la salida, por lo que el PF a la salida no es 1. La potencia es algo mayor que la rated porque la tension en bornas del stack de potencia es tb algo mayor
Note on B25: IF YES = '1' / NO = '0'

## V_0,92pu_DIG (hidden)
Inverter Voltage | 620 |  |  |  |  | P (W) | Q _Ii(VAr) | Vi_need | Q_Vdc (Var) | Q(Var) | P(kW) | Q_Ii(kVAr) | Vdc_min (V) | Q(kVAr) | S(kVA) | cos fi
Voltage operation pu | 0.92 |  |  | P_manual (kW), Q>0 | 3750 | 3750000 | 369061.8964 | 581.9127 | 3353688.3708 | 369061.8964 | 3750 | 369.0619 | 842.1351 | 369.0619 | 3768.1171 | 0.99519 | Capacitive
Line-Line Voltage (V) | 570.4 |  |  | P_manual (kW), Q<0 | 2846 | 2846000 | -1984391.8774 | 511.7066 | -43052528.8568 | -1984391.8774 | 2846 | -1984.3919 | 741.7404 | -1984.3919 | 3469.514 | 0.82029 | Inductive
Nm: Number of modules | 3 |  |  |  |  | 0 | 4062090.5539 | 676.9234 | 3655590.7355 | 3655590.7355 | 0 | 4062.0906 | 978.0005 | 3655.5907 | 3655.5907 | 0
f(Hz) | 50 | wg(Hz) | 314.1593 |  |  | 221434.5285 | 4055445.9533 | 676.764 | 3654544.8152 | 3654544.8152 | 221.4345 | 4055.446 | 977.7725 | 3654.5448 | 3661.2472 | 0.060481
Height (m) | 2700 |  |  |  |  | 442869.057 | 4035439.8998 | 676.2838 | 3651406.7743 | 3651406.7743 | 442.8691 | 4035.4399 | 977.0858 | 3651.4068 | 3678.1659 | 0.1204
Temperature Max (ºC) ( TM) | 33 | TM_H_corrected(ºC) | 44.25 |  |  | 664303.5855 | 4001851.6525 | 675.4768 | 3646175.7721 | 3646175.7721 | 664.3036 | 4001.8517 | 975.9318 | 3646.1758 | 3706.1971 | 0.17924
Vdc_min (Tmax) | 951.5 | Vdc_min(sat) | 951.5 |  |  | 885738.114 | 3954299.4979 | 674.3326 | 3638850.4066 | 3638850.4066 | 885.7381 | 3954.2995 | 974.2956 | 3638.8504 | 3745.0987 | 0.23651
TM_derating | 104.5% |  |  |  |  | 1107172.6425 | 3892218.0674 | 672.8359 | 3629428.712 | 3629428.712 | 1107.1726 | 3892.2181 | 972.1553 | 3629.4287 | 3794.5466 | 0.29178
Vdc_min derating | 114.9% |  |  |  |  | 1328607.171 | 3814822.1392 | 670.9653 | 3617908.1565 | 3617908.1565 | 1328.6072 | 3814.8221 | 969.4803 | 3617.9082 | 3854.148 | 0.34472
Total derating@ TM | 120% |  |  |  |  | 1550041.6995 | 3721051.0663 | 668.6919 | 3604285.6386 | 3604285.6386 | 1550.0417 | 3721.0511 | 966.2294 | 3604.2856 | 3923.4556 | 0.39507
Temperature Min (ºC) ( Tm) | -5 | Tm_H_corrected(ºC) | 6.25 |  |  | 1771476.228 | 3609483.5725 | 665.9769 | 3588557.4833 | 3588557.4833 | 1771.4762 | 3609.4836 | 962.347 | 3588.5575 | 4001.9836 | 0.44265
Vdc_max (Tmin) | 1130 | Vdc_max(sat) | 1130 |  |  | 1992910.7564 | 3478204.4442 | 662.7681 | 3570719.4366 | 3478204.4442 | 1992.9108 | 3478.2044 | 957.7583 | 3478.2044 | 4008.6905 | 0.49715
Tm_derating | 111.6% |  |  |  |  | 2214345.2849 | 3324588.1819 | 658.9934 | 3550766.6601 | 3324588.1819 | 2214.3453 | 3324.5882 | 952.3605 | 3324.5882 | 3994.5227 | 0.55435
Vdc_derating(V) | 106% |  |  |  |  | 2435779.8134 | 3144928.8539 | 654.5511 | 3528693.7243 | 3144928.8539 | 2435.7798 | 3144.9289 | 946.0081 | 3144.9289 | 3977.889 | 0.61233
Total derating@ Tm | 118.3% |  |  |  |  | 2657214.3419 | 2933759.2677 | 649.2909 | 3504494.6009 | 2933759.2677 | 2657.2143 | 2933.7593 | 938.4859 | 2933.7593 | 3958.2485 | 0.67131
[6 empty] | 2878648.8704 | 2682466.6051 | 642.9751 | 3478162.6549 | 2682466.6051 | 2878.6489 | 2682.4666 | 929.4544 | 2682.4666 | 3934.7486 | 0.7316
Derating factor for TM | 118.3% |  |  |  |  | 3100083.3989 | 2376035.6344 | 635.1886 | 3449690.6348 | 2376035.6344 | 3100.0834 | 2376.0356 | 918.3196 | 2376.0356 | 3905.901 | 0.79369
[6 empty] | 3321517.9274 | 1983366.4907 | 625.0689 | 3419070.663 | 1983366.4907 | 3321.5179 | 1983.3665 | 903.8485 | 1983.3665 | 3868.6204 | 0.85858
Vi_max (V) | 658.3916 |  |  |  |  | 3542952.4559 | 1411150.4534 | 610.0216 | 3386294.2242 | 1411150.4534 | 3542.9525 | 1411.1505 | 882.3308 | 1411.1505 | 3813.641 | 0.92902
Ii (A) | 1242.32 |  |  |  |  | 3598311.088 | 1200096.1792 | 604.377 | 3377762.1069 | 1200096.1792 | 3598.3111 | 1200.0962 | 874.2591 | 1200.0962 | 3793.1614 | 0.94863
P_max (W) (kW) | 3703995.7494 | P_base (kW) | 3703.9957 |  |  | 3653669.7202 | 906796.2559 | 596.4441 | 3369094.4913 | 906796.2559 | 3653.6697 | 906.7963 | 862.9151 | 906.7963 | 3764.5162 | 0.97055
Prated (W) | 3682094.038 | Prated (kW) | 3682.094 |  |  | 3709028.3523 | 369061.8964 | 581.701 | 3360291.2251 | 369061.8964 | 3709.0284 | 369.0619 | 841.8325 | 369.0619 | 3727.3446 | 0.99509
[6 empty] | 3764386.9844 | 369061.8964 | 581.9875 | 3351352.1535 | 369061.8964 | 3764.387 | 369.0619 | 842.2421 | 369.0619 | 3782.4352 | 0.99523
GPTech Inverter | 1 |  |  |  |  | 3819745.6165 | 369061.8964 | 582.2781 | 3342277.1189 | 369061.8964 | 3819.7456 | 369.0619 | 842.6576 | 369.0619 | 3837.5335 | 0.99536
Inverter output current (A) | 1250 |  |  |  |  | 3875104.2486 | 369061.8964 | 582.5727 | 3333065.9613 | 369061.8964 | 3875.1042 | 369.0619 | 843.079 | 369.0619 | 3892.6392 | 0.9955
[6 empty] | 3930462.8808 | 369061.8964 | 582.8715 | 3323718.5178 | 369061.8964 | 3930.4629 | 369.0619 | 843.5062 | 369.0619 | 3947.7519 | 0.99562
Set Point Calculation Tool (@Tmax) | [5 empty] | 3985821.5129 | 369061.8964 | 583.1743 | 3314234.6231 | 369061.8964 | 3985.8215 | 369.0619 | 843.9392 | 369.0619 | 4002.8714 | 0.99574
P | 2846 | 2846 |  |  |  | 4041180.145 | 369061.8964 | 583.4812 | 3304614.109 | 369061.8964 | 4041.1801 | 369.0619 | 844.3781 | 369.0619 | 4057.9975 | 0.99586
| Q_ind_lim | -1984.3919 |  |  |  | 4096538.7771 | 369061.8964 | 583.7922 | 3294856.8047 | 369061.8964 | 4096.5388 | 369.0619 | 844.8228 | 369.0619 | 4113.1298 | 0.99597
| Q_cap_lim | 2722.5157 |  |  |  | 4151897.4093 | 369061.8964 | 584.1072 | 3284962.5366 | 369061.8964 | 4151.8974 | 369.0619 | 845.2733 | 369.0619 | 4168.2681 | 0.99607
Q | 0 | 0 |  |  |  | 4207256.0414 | 369061.8964 | 584.4263 | 3274931.1283 | 369061.8964 | 4207.256 | 369.0619 | 845.7296 | 369.0619 | 4223.4121 | 0.99617
PF | 1 | Io(P,Q) (A) | 2880.6782 |  |  | 4262614.6735 | 369061.8964 | 584.7494 | 3264762.4009 | 369061.8964 | 4262.6147 | 369.0619 | 846.1917 | 369.0619 | 4278.5617 | 0.99627
Vdc_min(V) | 821.3797 |  |  |  |  | 4317973.3056 | 369061.8964 | 585.0766 | 3254456.1726 | 369061.8964 | 4317.9733 | 369.0619 | 846.6595 | 369.0619 | 4333.7167 | 0.99637
Vac_max(V) | 567.3984 |  |  |  |  | 4373331.9378 | 369061.8964 | 585.4078 | 3244012.2586 | 369061.8964 | 4373.3319 | 369.0619 | 847.1332 | 369.0619 | 4388.8767 | 0.99646
[6 empty] | 4428690.5699 | 369061.8964 | 585.743 | -42803779.8985 | 369061.8964 | 4428.6906 | 369.0619 | 847.6125 | 369.0619 | 4444.0417 | 0.99655
[6 empty] | 4373331.9378 | 369061.8964 | 585.4078 | -42814361.6855 | 369061.8964 | 4373.3319 | 369.0619 | 847.1332 | 369.0619 | 4388.8767 | 0.99646
[6 empty] | 4317973.3056 | 369061.8964 | 585.0766 | -42824805.5994 | 369061.8964 | 4317.9733 | 369.0619 | 846.6595 | 369.0619 | 4333.7167 | 0.99637
[6 empty] | 4262614.6735 | 369061.8964 | 584.7494 | -42835111.8278 | 369061.8964 | 4262.6147 | 369.0619 | 846.1917 | 369.0619 | 4278.5617 | 0.99627
[6 empty] | 4207256.0414 | 369061.8964 | 584.4263 | -42845280.5552 | 369061.8964 | 4207.256 | 369.0619 | 845.7296 | 369.0619 | 4223.4121 | 0.99617
[6 empty] | 4151897.4093 | 369061.8964 | 584.1072 | -42855311.9634 | 369061.8964 | 4151.8974 | 369.0619 | 845.2733 | 369.0619 | 4168.2681 | 0.99607
[6 empty] | 4096538.7771 | 369061.8964 | 583.7922 | -42865206.2316 | 369061.8964 | 4096.5388 | 369.0619 | 844.8228 | 369.0619 | 4113.1298 | 0.99597
[6 empty] | 4041180.145 | 369061.8964 | 583.4812 | -42874963.5359 | 369061.8964 | 4041.1801 | 369.0619 | 844.3781 | 369.0619 | 4057.9975 | 0.99586
[6 empty] | 3985821.5129 | 369061.8964 | 583.1743 | -42884584.05 | 369061.8964 | 3985.8215 | 369.0619 | 843.9392 | 369.0619 | 4002.8714 | 0.99574
[6 empty] | 3930462.8808 | 369061.8964 | 582.8715 | -42894067.9447 | 369061.8964 | 3930.4629 | 369.0619 | 843.5062 | 369.0619 | 3947.7519 | 0.99562
[6 empty] | 3875104.2486 | 369061.8964 | 582.5727 | -42903415.3881 | 369061.8964 | 3875.1042 | 369.0619 | 843.079 | 369.0619 | 3892.6392 | 0.9955
[6 empty] | 3819745.6165 | 369061.8964 | 582.2781 | -42912626.5457 | 369061.8964 | 3819.7456 | 369.0619 | 842.6576 | 369.0619 | 3837.5335 | 0.99536
[6 empty] | 3764386.9844 | 369061.8964 | 581.9875 | -42921701.5803 | 369061.8964 | 3764.387 | 369.0619 | 842.2421 | 369.0619 | 3782.4352 | 0.99523
[6 empty] | 3709028.3523 | 369061.8964 | 581.701 | -42930640.652 | 369061.8964 | 3709.0284 | 369.0619 | 841.8325 | 369.0619 | 3727.3446 | 0.99509
[6 empty] | 3653669.7202 | -168672.4631 | 566.406 | -42939443.9182 | -168672.4631 | 3653.6697 | -168.6725 | 819.9606 | -168.6725 | 3657.561 | 0.99894
[6 empty] | 3598311.088 | -461972.3863 | 557.9335 | -42948111.5338 | -461972.3863 | 3598.3111 | -461.9724 | 807.8449 | -461.9724 | 3627.8453 | 0.99186
[6 empty] | 3542952.4559 | -673026.6605 | 551.7563 | -42956643.651 | -673026.6605 | 3542.9525 | -673.0267 | 799.0115 | -673.0267 | 3606.3107 | 0.98243
[6 empty] | 3321517.9274 | -1245242.6979 | 534.6496 | -42989420.0898 | -1245242.6979 | 3321.5179 | -1245.2427 | 774.5489 | -1245.2427 | 3547.2681 | 0.93636
[6 empty] | 3100083.3989 | -1637911.8416 | 522.5867 | -43020040.0617 | -1637911.8416 | 3100.0834 | -1637.9118 | 757.2989 | -1637.9118 | 3506.1763 | 0.88418
[6 empty] | 2878648.8704 | -1944342.8123 | 512.976 | -43048512.0817 | -1944342.8123 | 2878.6489 | -1944.3428 | 743.5556 | -1944.3428 | 3473.7715 | 0.82868
[6 empty] | 2657214.3419 | -2195635.4749 | 504.9581 | -43074844.0278 | -2195635.4749 | 2657.2143 | -2195.6355 | 732.0901 | -2195.6355 | 3446.9701 | 0.77088
[6 empty] | 2435779.8134 | -2406805.0611 | 498.1207 | -43099043.1511 | -2406805.0611 | 2435.7798 | -2406.8051 | 722.3125 | -2406.8051 | 3424.2859 | 0.71132
[6 empty] | 2214345.2849 | -2586464.3891 | 492.2287 | -43121116.087 | -2586464.3891 | 2214.3453 | -2586.4644 | 713.887 | -2586.4644 | 3404.8676 | 0.65035
[6 empty] | 1992910.7564 | -2740080.6513 | 487.1343 | -43141068.8635 | -2740080.6513 | 1992.9108 | -2740.0807 | 706.6021 | -2740.0807 | 3388.1758 | 0.5882
[6 empty] | 1771476.228 | -2871359.7797 | 482.7381 | -43158906.9102 | -2871359.7797 | 1771.4762 | -2871.3598 | 700.3155 | -2871.3598 | 3373.8457 | 0.52506
[6 empty] | 1550041.6995 | -2982927.2735 | 478.9703 | -43174635.0655 | -2982927.2735 | 1550.0417 | -2982.9273 | 694.9275 | -2982.9273 | 3361.6193 | 0.4611
[6 empty] | 1328607.171 | -3076698.3463 | 475.7804 | -43188257.5833 | -3076698.3463 | 1328.6072 | -3076.6983 | 690.3659 | -3076.6983 | 3351.3087 | 0.39644
[6 empty] | 1107172.6425 | -3154094.2746 | 473.1313 | -43199778.1389 | -3154094.2746 | 1107.1726 | -3154.0943 | 686.5778 | -3154.0943 | 3342.7746 | 0.33121
[6 empty] | 885738.114 | -3216175.705 | 470.9957 | -43209199.8335 | -3216175.705 | 885.7381 | -3216.1757 | 683.5238 | -3216.1757 | 3335.9134 | 0.26552
[6 empty] | 664303.5855 | -3263727.8596 | 469.3532 | -43216525.199 | -3263727.8596 | 664.3036 | -3263.7279 | 681.1751 | -3263.7279 | 3330.6484 | 0.19945
[6 empty] | 442869.057 | -3297316.107 | 468.1897 | -43221756.2011 | -3297316.107 | 442.8691 | -3297.3161 | 679.5112 | -3297.3161 | 3326.9245 | 0.13312
[6 empty] | 221434.5285 | -3317322.1605 | 467.4952 | -43224894.242 | -3317322.1605 | 221.4345 | -3317.3222 | 678.5182 | -3317.3222 | 3324.7044 | 0.066603
[6 empty] | -5.2387e-10 | -3323966.7611 | 467.2644 | -43225940.1623 | -3323966.7611 | -5.2387e-13 | -3323.9668 | 678.1881 | -3323.9668 | 3323.9668 | -1.576e-16
Note on B22: Autor: P_max no se da con reactiva 0 a la salida, por lo que el PF a la salida no es 1. La potencia es algo mayor que la rated porque la tension en bornas del stack de potencia es tb algo mayor
Note on B25: IF YES = '1' / NO = '0'

## V_0,94pu_DIG (hidden)
Inverter Voltage | 620 |  |  |  |  | P (W) | Q _Ii(VAr) | Vi_need | Q_Vdc (Var) | Q(Var) | P(kW) | Q_Ii(kVAr) | Vdc_min (V) | Q(kVAr) | S(kVA) | cos fi
Voltage operation pu | 0.94 |  |  | P_manual (kW), Q>0 | 3750 | 3750000 | 804069.5547 | 605.2 | 3000199.5328 | 804069.5547 | 3750 | 804.0696 | 875.436 | 804.0696 | 3835.235 | 0.97778 | Capacitive
Line-Line Voltage (V) | 582.8 |  |  | P_manual (kW), Q<0 | 2846 | 2846000 | -2092249.883 | 521.7264 | -44435402.1945 | -2092249.883 | 2846 | -2092.2499 | 756.0688 | -2092.2499 | 3532.3116 | 0.8057 | Inductive
Nm: Number of modules | 3 |  |  |  |  | 0 | 4158594.3699 | 689.3603 | 3295597.3339 | 3295597.3339 | 0 | 4158.5944 | 995.7852 | 3295.5973 | 3295.5973 | 0
f(Hz) | 50 | wg(Hz) | 314.1593 |  |  | 221434.5285 | 4152091.3905 | 689.207 | 3294573.6682 | 3294573.6682 | 221.4345 | 4152.0914 | 995.5661 | 3294.5737 | 3302.0068 | 0.067061
Height (m) | 2700 |  |  |  |  | 442869.057 | 4132514.7409 | 688.7456 | 3291502.4085 | 3291502.4085 | 442.8691 | 4132.5147 | 994.9062 | 3291.5024 | 3321.1626 | 0.13335
Temperature Max (ºC) ( TM) | 33 | TM_H_corrected(ºC) | 44.25 |  |  | 664303.5855 | 4099657.7121 | 687.9705 | 3286382.7669 | 3286382.7669 | 664.3036 | 4099.6577 | 993.7978 | 3286.3828 | 3352.8512 | 0.19813
Vdc_min (Tmax) | 951.5 | Vdc_min(sat) | 951.5 |  |  | 885738.114 | 4053163.423 | 686.8721 | 3279213.4287 | 3279213.4287 | 885.7381 | 4053.1634 | 992.2271 | 3279.2134 | 3396.7297 | 0.26076
TM_derating | 104.5% |  |  |  |  | 1107172.6425 | 3992504.591 | 685.4365 | 3269992.5515 | 3269992.5515 | 1107.1726 | 3992.5046 | 990.1742 | 3269.9926 | 3452.3445 | 0.3207
Vdc_min derating | 114.9% |  |  |  |  | 1328607.171 | 3916951.4344 | 683.6441 | 3258717.7619 | 3258717.7619 | 1328.6072 | 3916.9514 | 987.6111 | 3258.7178 | 3519.1531 | 0.37754
Total derating@ TM | 120% |  |  |  |  | 1550041.6995 | 3825522.7838 | 681.4689 | 3245386.1532 | 3245386.1532 | 1550.0417 | 3825.5228 | 984.5005 | 3245.3862 | 3596.5484 | 0.43098
Temperature Min (ºC) ( Tm) | -5 | Tm_H_corrected(ºC) | 6.25 |  |  | 1771476.228 | 3716911.8999 | 678.8758 | 3229994.2814 | 3229994.2814 | 1771.4762 | 3716.9119 | 980.7923 | 3229.9943 | 3683.8826 | 0.48087
Vdc_max (Tmin) | 1130 | Vdc_max(sat) | 1130 |  |  | 1992910.7564 | 3589371.9505 | 675.818 | 3212538.1603 | 3212538.1603 | 1992.9108 | 3589.372 | 976.4197 | 3212.5382 | 3780.4887 | 0.52716
Tm_derating | 111.6% |  |  |  |  | 2214345.2849 | 3440533.3006 | 672.232 | 3193013.2571 | 3193013.2571 | 2214.3453 | 3440.5333 | 971.2918 | 3193.0133 | 3885.6993 | 0.56987
Vdc_derating(V) | 106% |  |  |  |  | 2435779.8134 | 3267097.7617 | 668.0291 | 3171414.4859 | 3171414.4859 | 2435.7798 | 3267.0978 | 965.2817 | 3171.4145 | 3998.8615 | 0.60912
Total derating@ Tm | 118.3% |  |  |  |  | 2657214.3419 | 3064292.4759 | 663.0808 | 3147736.201 | 3064292.4759 | 2657.2143 | 3064.2925 | 958.2055 | 3064.2925 | 4055.9433 | 0.65514
[6 empty] | 2878648.8704 | 2824803.6005 | 657.1893 | 3121972.1897 | 2824803.6005 | 2878.6489 | 2824.8036 | 949.7807 | 2824.8036 | 4033.1296 | 0.71375
Derating factor for TM | 118.3% |  |  |  |  | 3100083.3989 | 2536413.7024 | 650.0241 | 3094115.6639 | 2536413.7024 | 3100.0834 | 2536.4137 | 939.5344 | 2536.4137 | 4005.4852 | 0.77396
[6 empty] | 3321517.9274 | 2175645.9274 | 640.9478 | 3064159.2511 | 2175645.9274 | 3321.5179 | 2175.6459 | 926.5553 | 2175.6459 | 3970.6318 | 0.83652
Vi_max (V) | 658.3916 |  |  |  |  | 3542952.4559 | 1683500.686 | 628.3548 | 3032094.984 | 1683500.686 | 3542.9525 | 1683.5007 | 908.5474 | 1683.5007 | 3922.5867 | 0.90322
Ii (A) | 1242.32 |  |  |  |  | 3598311.088 | 1521081.7266 | 624.1431 | 3023748.5739 | 1521081.7266 | 3598.3111 | 1521.0817 | 902.5247 | 1521.0817 | 3906.6011 | 0.92108
P_max (W) (kW) | 3784517.3961 | P_base (kW) | 3784.5174 |  |  | 3653669.7202 | 1327927.7954 | 619.0971 | 3015269.7502 | 1327927.7954 | 3653.6697 | 1327.9278 | 895.3089 | 1327.9278 | 3887.5049 | 0.93985
Prated (W) | 3762139.5605 | Prated (kW) | 3762.1396 |  |  | 3709028.3523 | 1078817.8405 | 612.528 | 3006658.3706 | 1078817.8405 | 3709.0284 | 1078.8178 | 885.915 | 1078.8178 | 3862.7373 | 0.96021
[6 empty] | 3764386.9844 | 644653.3445 | 600.9072 | 2997914.2903 | 644653.3445 | 3764.387 | 644.6533 | 869.2972 | 644.6533 | 3819.1867 | 0.98565
GPTech Inverter | 1 |  |  |  |  | 3819745.6165 | 385282.4807 | 594.0855 | 2989037.3621 | 385282.4807 | 3819.7456 | 385.2825 | 859.5422 | 385.2825 | 3839.1274 | 0.99495
Inverter output current (A) | 1250 |  |  |  |  | 3875104.2486 | 385282.4807 | 594.3621 | 2980027.4362 | 385282.4807 | 3875.1042 | 385.2825 | 859.9378 | 385.2825 | 3894.2105 | 0.99509
[6 empty] | 3930462.8808 | 385282.4807 | 594.6426 | 2970884.3606 | 385282.4807 | 3930.4629 | 385.2825 | 860.3389 | 385.2825 | 3949.3013 | 0.99523
Set Point Calculation Tool (@Tmax) | [5 empty] | 3985821.5129 | 385282.4807 | 594.9269 | 2961607.9805 | 385282.4807 | 3985.8215 | 385.2825 | 860.7455 | 385.2825 | 4004.3995 | 0.99536
P | 2846 | 2846 |  |  |  | 4041180.145 | 385282.4807 | 595.2151 | 2952198.1389 | 385282.4807 | 4041.1801 | 385.2825 | 861.1576 | 385.2825 | 4059.5048 | 0.99549
| Q_ind_lim | -2092.2499 |  |  |  | 4096538.7771 | 385282.4807 | 595.5071 | 2942654.676 | 385282.4807 | 4096.5388 | 385.2825 | 861.5752 | 385.2825 | 4114.6169 | 0.99561
| Q_cap_lim | 2862.8148 |  |  |  | 4151897.4093 | 385282.4807 | 595.803 | 2932977.4297 | 385282.4807 | 4151.8974 | 385.2825 | 861.9982 | 385.2825 | 4169.7356 | 0.99572
Q | 0 | 0 |  |  |  | 4207256.0414 | 385282.4807 | 596.1026 | 2923166.2353 | 385282.4807 | 4207.256 | 385.2825 | 862.4268 | 385.2825 | 4224.8605 | 0.99583
PF | 1 | Io(P,Q) (A) | 2819.3872 |  |  | 4262614.6735 | 385282.4807 | 596.4061 | 2913220.9254 | 385282.4807 | 4262.6147 | 385.2825 | 862.8607 | 385.2825 | 4279.9914 | 0.99594
Vdc_min(V) | 838.3254 |  |  |  |  | 4317973.3056 | 385282.4807 | 596.7134 | 2903141.3302 | 385282.4807 | 4317.9733 | 385.2825 | 863.3001 | 385.2825 | 4335.1281 | 0.99604
Vac_max(V) | 579.2486 |  |  |  |  | 4373331.9378 | 385282.4807 | 597.0245 | 2892927.2773 | 385282.4807 | 4373.3319 | 385.2825 | 863.745 | 385.2825 | 4390.2705 | 0.99614
[6 empty] | 4428690.5699 | 385282.4807 | 597.3394 | 2882578.5916 | 385282.4807 | 4428.6906 | 385.2825 | 864.1953 | 385.2825 | 4445.4182 | 0.99624
[6 empty] | 4373331.9378 | 385282.4807 | 597.0245 | -44202427.2224 | 385282.4807 | 4373.3319 | 385.2825 | 863.745 | 385.2825 | 4390.2705 | 0.99614
[6 empty] | 4317973.3056 | 385282.4807 | 596.7134 | -44212641.2754 | 385282.4807 | 4317.9733 | 385.2825 | 863.3001 | 385.2825 | 4335.1281 | 0.99604
[6 empty] | 4262614.6735 | 385282.4807 | 596.4061 | -44222720.8705 | 385282.4807 | 4262.6147 | 385.2825 | 862.8607 | 385.2825 | 4279.9914 | 0.99594
[6 empty] | 4207256.0414 | 385282.4807 | 596.1026 | -44232666.1804 | 385282.4807 | 4207.256 | 385.2825 | 862.4268 | 385.2825 | 4224.8605 | 0.99583
[6 empty] | 4151897.4093 | 385282.4807 | 595.803 | -44242477.3749 | 385282.4807 | 4151.8974 | 385.2825 | 861.9982 | 385.2825 | 4169.7356 | 0.99572
[6 empty] | 4096538.7771 | 385282.4807 | 595.5071 | -44252154.6212 | 385282.4807 | 4096.5388 | 385.2825 | 861.5752 | 385.2825 | 4114.6169 | 0.99561
[6 empty] | 4041180.145 | 385282.4807 | 595.2151 | -44261698.084 | 385282.4807 | 4041.1801 | 385.2825 | 861.1576 | 385.2825 | 4059.5048 | 0.99549
[6 empty] | 3985821.5129 | 385282.4807 | 594.9269 | -44271107.9257 | 385282.4807 | 3985.8215 | 385.2825 | 860.7455 | 385.2825 | 4004.3995 | 0.99536
[6 empty] | 3930462.8808 | 385282.4807 | 594.6426 | -44280384.3057 | 385282.4807 | 3930.4629 | 385.2825 | 860.3389 | 385.2825 | 3949.3013 | 0.99523
[6 empty] | 3875104.2486 | 385282.4807 | 594.3621 | -44289527.3814 | 385282.4807 | 3875.1042 | 385.2825 | 859.9378 | 385.2825 | 3894.2105 | 0.99509
[6 empty] | 3819745.6165 | 385282.4807 | 594.0855 | -44298537.3072 | 385282.4807 | 3819.7456 | 385.2825 | 859.5422 | 385.2825 | 3839.1274 | 0.99495
[6 empty] | 3764386.9844 | 125911.6169 | 586.7209 | -44307414.2355 | 125911.6169 | 3764.387 | 125.9116 | 849.0108 | 125.9116 | 3766.4921 | 0.99944
[6 empty] | 3709028.3523 | -308252.8791 | 574.5784 | -44316158.3158 | -308252.8791 | 3709.0284 | -308.2529 | 831.6471 | -308.2529 | 3721.8156 | 0.99656
[6 empty] | 3653669.7202 | -557362.834 | 567.4941 | -44324769.6954 | -557362.834 | 3653.6697 | -557.3628 | 821.5165 | -557.3628 | 3695.9377 | 0.98856
[6 empty] | 3598311.088 | -750516.7652 | 561.9396 | -44333248.519 | -750516.7652 | 3598.3111 | -750.5168 | 813.5737 | -750.5168 | 3675.7473 | 0.97893
[6 empty] | 3542952.4559 | -912935.7246 | 557.2262 | -44341594.9291 | -912935.7246 | 3542.9525 | -912.9357 | 806.8334 | -912.9357 | 3658.6833 | 0.96837
[6 empty] | 3321517.9274 | -1405080.966 | 542.694 | -44373659.1962 | -1405080.966 | 3321.5179 | -1405.081 | 786.0524 | -1405.081 | 3606.485 | 0.92098
[6 empty] | 3100083.3989 | -1765848.741 | 531.789 | -44403615.6091 | -1765848.741 | 3100.0834 | -1765.8487 | 770.4582 | -1765.8487 | 3567.7358 | 0.86892
[6 empty] | 2878648.8704 | -2054238.6391 | 522.9082 | -44431472.1349 | -2054238.6391 | 2878.6489 | -2054.2386 | 757.7587 | -2054.2386 | 3536.4552 | 0.81399
[6 empty] | 2657214.3419 | -2293727.5145 | 515.417 | -44457236.1461 | -2293727.5145 | 2657.2143 | -2293.7275 | 747.0463 | -2293.7275 | 3510.2669 | 0.75698
[6 empty] | 2435779.8134 | -2496532.8003 | 508.9871 | -44480914.431 | -2496532.8003 | 2435.7798 | -2496.5328 | 737.8515 | -2496.5328 | 3487.9363 | 0.69834
[6 empty] | 2214345.2849 | -2669968.3392 | 503.4232 | -44502513.2023 | -2669968.3392 | 2214.3453 | -2669.9683 | 729.8952 | -2669.9683 | 3468.7254 | 0.63837
[6 empty] | 1992910.7564 | -2818806.989 | 498.5989 | -44522038.1055 | -2818806.989 | 1992.9108 | -2818.807 | 722.9964 | -2818.807 | 3452.1538 | 0.57729
[6 empty] | 1771476.228 | -2946346.9385 | 494.4274 | -44539494.2265 | -2946346.9385 | 1771.4762 | -2946.3469 | 717.0312 | -2946.3469 | 3437.8901 | 0.51528
[6 empty] | 1550041.6995 | -3054957.8224 | 490.8472 | -44554886.0984 | -3054957.8224 | 1550.0417 | -3054.9578 | 711.9115 | -3054.9578 | 3425.6965 | 0.45247
[6 empty] | 1328607.171 | -3146386.473 | 487.813 | -44568217.707 | -3146386.473 | 1328.6072 | -3146.3865 | 707.5725 | -3146.3865 | 3415.3982 | 0.38901
[6 empty] | 1107172.6425 | -3221939.6296 | 485.2913 | -44579492.4966 | -3221939.6296 | 1107.1726 | -3221.9396 | 703.9665 | -3221.9396 | 3406.8646 | 0.32498
[6 empty] | 885738.114 | -3282598.4616 | 483.2572 | -44588713.3739 | -3282598.4616 | 885.7381 | -3282.5985 | 701.0578 | -3282.5985 | 3399.9977 | 0.26051
[6 empty] | 664303.5855 | -3329092.7507 | 481.6922 | -44595882.712 | -3329092.7507 | 664.3036 | -3329.0928 | 698.8199 | -3329.0928 | 3394.725 | 0.19569
[6 empty] | 442869.057 | -3361949.7795 | 480.5833 | -44601002.3537 | -3361949.7795 | 442.8691 | -3361.9498 | 697.2341 | -3361.9498 | 3390.9939 | 0.1306
[6 empty] | 221434.5285 | -3381526.4291 | 479.9213 | -44604073.6134 | -3381526.4291 | 221.4345 | -3381.5264 | 696.2874 | -3381.5264 | 3388.7688 | 0.065344
[6 empty] | -5.2387e-10 | -3388029.4085 | 479.7012 | -44605097.2791 | -3388029.4085 | -5.2387e-13 | -3388.0294 | 695.9727 | -3388.0294 | 3388.0294 | -1.5462e-16
Note on B22: Autor: P_max no se da con reactiva 0 a la salida, por lo que el PF a la salida no es 1. La potencia es algo mayor que la rated porque la tension en bornas del stack de potencia es tb algo mayor
Note on B25: IF YES = '1' / NO = '0'

## V_0,96pu_DIG (hidden)
Inverter Voltage | 620 |  |  |  |  | P (W) | Q _Ii(VAr) | Vi_need | Q_Vdc (Var) | Q(Var) | P(kW) | Q_Ii(kVAr) | Vdc_min (V) | Q(kVAr) | S(kVA) | cos fi
Voltage operation pu | 0.96 |  |  | P_manual (kW), Q>0 | 3750 | 3750000 | 1289373.926 | 629.4323 | 2627734.1368 | 1289373.926 | 3750 | 1289.3739 | 910.0882 | 1289.3739 | 3965.4741 | 0.94566 | Capacitive
Line-Line Voltage (V) | 595.2 |  |  | P_manual (kW), Q<0 | 2846 | 2846000 | -2196316.567 | 531.9534 | -45836819.6061 | -2196316.567 | 2846 | -2196.3166 | 770.6934 | -2196.3166 | 3594.9301 | 0.79167 | Inductive
Nm: Number of modules | 3 |  |  |  |  | 0 | 4255447.0157 | 701.7971 | 2916903.3892 | 2916903.3892 | 0 | 4255.447 | 1013.5698 | 2916.9034 | 2916.9034 | 0
f(Hz) | 50 | wg(Hz) | 314.1593 |  |  | 221434.5285 | 4249079.7416 | 701.6497 | 2915901.0507 | 2915901.0507 | 221.4345 | 4249.0797 | 1013.3591 | 2915.9011 | 2924.2969 | 0.075722
Height (m) | 2700 |  |  |  |  | 442869.057 | 4229914.3752 | 701.206 | 2912893.7889 | 2912893.7889 | 442.8691 | 4229.9144 | 1012.7246 | 2912.8938 | 2946.3678 | 0.15031
Temperature Max (ºC) ( TM) | 33 | TM_H_corrected(ºC) | 44.25 |  |  | 664303.5855 | 4197757.0704 | 700.4609 | 2907880.8639 | 2907880.8639 | 664.3036 | 4197.7571 | 1011.6591 | 2907.8809 | 2982.7957 | 0.22271
Vdc_min (Tmax) | 951.5 | Vdc_min(sat) | 951.5 |  |  | 885738.114 | 4152273.651 | 699.4056 | 2900861.0417 | 2900861.0417 | 885.7381 | 4152.2737 | 1010.15 | 2900.861 | 3033.0722 | 0.29203
TM_derating | 104.5% |  |  |  |  | 1107172.6425 | 4092971.5211 | 698.0273 | 2891832.5928 | 2891832.5928 | 1107.1726 | 4092.9715 | 1008.1791 | 2891.8326 | 3096.5347 | 0.35755
Vdc_min derating | 114.9% |  |  |  |  | 1328607.171 | 4019171.115 | 696.3083 | 2880793.2896 | 2880793.2896 | 1328.6072 | 4019.1711 | 1005.7208 | 2880.7933 | 3172.4071 | 0.4188
Total derating@ TM | 120% |  |  |  |  | 1550041.6995 | 3929962.7329 | 694.2246 | 2867740.404 | 2867740.404 | 1550.0417 | 3929.9627 | 1002.7412 | 2867.7404 | 3259.8411 | 0.4755
Temperature Min (ºC) ( Tm) | -5 | Tm_H_corrected(ºC) | 6.25 |  |  | 1771476.228 | 3824141.6735 | 691.7448 | 2852670.7039 | 2852670.7039 | 1771.4762 | 3824.1417 | 999.1951 | 2852.6707 | 3357.9545 | 0.52755
Vdc_max (Tmin) | 1130 | Vdc_max(sat) | 1130 |  |  | 1992910.7564 | 3700109.3245 | 688.8269 | 2835580.4492 | 2835580.4492 | 1992.9108 | 3700.1093 | 995.0225 | 2835.5804 | 3465.8635 | 0.57501
Tm_derating | 111.6% |  |  |  |  | 2214345.2849 | 3555717.8264 | 685.4144 | 2816465.3871 | 2816465.3871 | 2214.3453 | 3555.7178 | 990.1426 | 2816.4654 | 3582.7088 | 0.61806
Vdc_derating(V) | 106% |  |  |  |  | 2435779.8134 | 3388015.3291 | 681.4295 | 2795320.7468 | 2795320.7468 | 2435.7798 | 3388.0153 | 984.4441 | 2795.3207 | 3707.6733 | 0.65696
Total derating@ Tm | 118.3% |  |  |  |  | 2657214.3419 | 3192802.8612 | 676.7613 | 2772141.2336 | 2772141.2336 | 2657.2143 | 3192.8029 | 977.7687 | 2772.1412 | 3839.9942 | 0.69198
[6 empty] | 2878648.8704 | 2963799.5985 | 671.2437 | 2746921.0219 | 2746921.0219 | 2878.6489 | 2963.7996 | 969.8785 | 2746.921 | 3978.969 | 0.72347
Derating factor for TM | 118.3% |  |  |  |  | 3100083.3989 | 2690886.2492 | 664.6084 | 2719653.748 | 2690886.2492 | 3100.0834 | 2690.8862 | 960.39 | 2690.8862 | 4105.044 | 0.75519
[6 empty] | 3321517.9274 | 2355749.0297 | 656.3684 | 2690332.5018 | 2355749.0297 | 3321.5179 | 2355.749 | 948.6068 | 2355.749 | 4072.1045 | 0.81568
Vi_max (V) | 658.3916 |  |  |  |  | 3542952.4559 | 1917662.9816 | 645.4386 | 2658949.8181 | 1917662.9816 | 3542.9525 | 1917.663 | 932.9772 | 1917.663 | 4028.6404 | 0.87944
Ii (A) | 1242.32 |  |  |  |  | 3598311.088 | 1781109.9089 | 641.9937 | 2650781.1191 | 1781109.9089 | 3598.3111 | 1781.1099 | 928.051 | 1781.1099 | 4014.9963 | 0.89622
P_max (W) (kW) | 3865039.0428 | P_base (kW) | 3865.039 |  |  | 3653669.7202 | 1626961.2498 | 638.0826 | 2642482.9501 | 1626961.2498 | 3653.6697 | 1626.9612 | 922.4581 | 1626.9612 | 3999.5381 | 0.91352
Prated (W) | 3842185.0831 | Prated (kW) | 3842.1851 |  |  | 3709028.3523 | 1447463.6955 | 633.4979 | 2634055.1778 | 1447463.6955 | 3709.0284 | 1447.4637 | 915.902 | 1447.4637 | 3981.4624 | 0.93157
[6 empty] | 3764386.9844 | 1226221.9497 | 627.8009 | 2625497.6666 | 1226221.9497 | 3764.387 | 1226.2219 | 907.7552 | 1226.2219 | 3959.0693 | 0.95083
GPTech Inverter | 1 |  |  |  |  | 3819745.6165 | 911497.6354 | 619.6064 | 2616810.2787 | 911497.6354 | 3819.7456 | 911.4976 | 896.0372 | 911.4976 | 3926.9943 | 0.97269
Inverter output current (A) | 1250 |  |  |  |  | 3875104.2486 | 401851.8948 | 606.2034 | 2607992.8739 | 401851.8948 | 3875.1042 | 401.8519 | 876.8708 | 401.8519 | 3895.8847 | 0.99467
[6 empty] | 3930462.8808 | 401851.8948 | 606.467 | 2599045.3097 | 401851.8948 | 3930.4629 | 401.8519 | 877.2479 | 401.8519 | 3950.9522 | 0.99481
Set Point Calculation Tool (@Tmax) | [5 empty] | 3985821.5129 | 401851.8948 | 606.7343 | 2589967.4414 | 401851.8948 | 3985.8215 | 401.8519 | 877.6301 | 401.8519 | 4006.0277 | 0.99496
P | 2846 | 2846 |  |  |  | 4041180.145 | 401851.8948 | 607.0053 | 2580759.1219 | 401851.8948 | 4041.1801 | 401.8519 | 878.0175 | 401.8519 | 4061.1109 | 0.99509
| Q_ind_lim | -2196.3166 |  |  |  | 4096538.7771 | 401851.8948 | 607.2798 | 2571420.2017 | 401851.8948 | 4096.5388 | 401.8519 | 878.4101 | 401.8519 | 4116.2015 | 0.99522
| Q_cap_lim | 2750.7681 |  |  |  | 4151897.4093 | 401851.8948 | 607.5579 | 2561950.529 | 401851.8948 | 4151.8974 | 401.8519 | 878.8079 | 401.8519 | 4171.2992 | 0.99535
Q | 0 | 0 |  |  |  | 4207256.0414 | 401851.8948 | 607.8397 | 2552349.9498 | 401851.8948 | 4207.256 | 401.8519 | 879.2108 | 401.8519 | 4226.4037 | 0.99547
PF | 1 | Io(P,Q) (A) | 2760.65 |  |  | 4262614.6735 | 401851.8948 | 608.125 | 2542618.3073 | 401851.8948 | 4262.6147 | 401.8519 | 879.6188 | 401.8519 | 4281.5148 | 0.99559
Vdc_min(V) | 855.3126 |  |  |  |  | 4317973.3056 | 401851.8948 | 608.414 | 2532755.4428 | 401851.8948 | 4317.9733 | 401.8519 | 880.032 | 401.8519 | 4336.6322 | 0.9957
Vac_max(V) | 591.1277 |  |  |  |  | 4373331.9378 | 401851.8948 | 608.7065 | 2522761.1948 | 401851.8948 | 4373.3319 | 401.8519 | 880.4503 | 401.8519 | 4391.7556 | 0.9958
[6 empty] | 4428690.5699 | 401851.8948 | 609.0026 | 2512635.3997 | 401851.8948 | 4428.6906 | 401.8519 | 880.8738 | 401.8519 | 4446.8849 | 0.99591
[6 empty] | 4373331.9378 | 401851.8948 | 608.7065 | -45608812.7447 | 401851.8948 | 4373.3319 | 401.8519 | 880.4503 | 401.8519 | 4391.7556 | 0.9958
[6 empty] | 4317973.3056 | 401851.8948 | 608.414 | -45618806.9926 | 401851.8948 | 4317.9733 | 401.8519 | 880.032 | 401.8519 | 4336.6322 | 0.9957
[6 empty] | 4262614.6735 | 401851.8948 | 608.125 | -45628669.8572 | 401851.8948 | 4262.6147 | 401.8519 | 879.6188 | 401.8519 | 4281.5148 | 0.99559
[6 empty] | 4207256.0414 | 401851.8948 | 607.8397 | -45638401.4996 | 401851.8948 | 4207.256 | 401.8519 | 879.2108 | 401.8519 | 4226.4037 | 0.99547
[6 empty] | 4151897.4093 | 401851.8948 | 607.5579 | -45648002.0789 | 401851.8948 | 4151.8974 | 401.8519 | 878.8079 | 401.8519 | 4171.2992 | 0.99535
[6 empty] | 4096538.7771 | 401851.8948 | 607.2798 | -45657471.7515 | 401851.8948 | 4096.5388 | 401.8519 | 878.4101 | 401.8519 | 4116.2015 | 0.99522
[6 empty] | 4041180.145 | 401851.8948 | 607.0053 | -45666810.6717 | 401851.8948 | 4041.1801 | 401.8519 | 878.0175 | 401.8519 | 4061.1109 | 0.99509
[6 empty] | 3985821.5129 | 401851.8948 | 606.7343 | -45676018.9912 | 401851.8948 | 3985.8215 | 401.8519 | 877.6301 | 401.8519 | 4006.0277 | 0.99496
[6 empty] | 3930462.8808 | 401851.8948 | 606.467 | -45685096.8595 | 401851.8948 | 3930.4629 | 401.8519 | 877.2479 | 401.8519 | 3950.9522 | 0.99481
[6 empty] | 3875104.2486 | 401851.8948 | 606.2034 | -45694044.4237 | 401851.8948 | 3875.1042 | 401.8519 | 876.8708 | 401.8519 | 3895.8847 | 0.99467
[6 empty] | 3819745.6165 | -107793.8458 | 592.2895 | -45702861.8285 | -107793.8458 | 3819.7456 | -107.7938 | 856.974 | -107.7938 | 3821.2663 | 0.9996
[6 empty] | 3764386.9844 | -422518.1602 | 583.5966 | -45711549.2164 | -422518.1602 | 3764.387 | -422.5182 | 844.5432 | -422.5182 | 3788.0247 | 0.99376
[6 empty] | 3709028.3523 | -643759.906 | 577.4075 | -45720106.7276 | -643759.906 | 3709.0284 | -643.7599 | 835.6927 | -643.7599 | 3764.4811 | 0.98527
[6 empty] | 3653669.7202 | -823257.4603 | 572.3369 | -45728534.4999 | -823257.4603 | 3653.6697 | -823.2575 | 828.4418 | -823.2575 | 3745.2711 | 0.97554
[6 empty] | 3598311.088 | -977406.1194 | 567.9463 | -45736832.669 | -977406.1194 | 3598.3111 | -977.4061 | 822.1632 | -977.4061 | 3728.6949 | 0.96503
[6 empty] | 3542952.4559 | -1113959.1921 | 564.0283 | -45745001.368 | -1113959.1921 | 3542.9525 | -1113.9592 | 816.5605 | -1113.9592 | 3713.949 | 0.95396
[6 empty] | 3321517.9274 | -1552045.2401 | 551.2708 | -45776384.0517 | -1552045.2401 | 3321.5179 | -1552.0452 | 798.3173 | -1552.0452 | 3666.2414 | 0.90597
[6 empty] | 3100083.3989 | -1887182.4596 | 541.3083 | -45805705.2978 | -1887182.4596 | 3100.0834 | -1887.1825 | 784.0709 | -1887.1825 | 3629.3215 | 0.85418
[6 empty] | 2878648.8704 | -2160095.809 | 533.058 | -45832972.5717 | -2160095.809 | 2878.6489 | -2160.0958 | 772.2729 | -2160.0958 | 3598.9767 | 0.79985
[6 empty] | 2657214.3419 | -2389099.0716 | 526.0353 | -45858192.7835 | -2389099.0716 | 2657.2143 | -2389.0991 | 762.2304 | -2389.0991 | 3573.3153 | 0.74363
[6 empty] | 2435779.8134 | -2584311.5395 | 519.9739 | -45881372.2967 | -2584311.5395 | 2435.7798 | -2584.3115 | 753.5627 | -2584.3115 | 3551.2941 | 0.68589
[6 empty] | 2214345.2849 | -2752014.0369 | 514.7097 | -45902516.9369 | -2752014.0369 | 2214.3453 | -2752.014 | 746.0349 | -2752.014 | 3532.2665 | 0.62689
[6 empty] | 1992910.7564 | -2896405.5349 | 510.1338 | -45921631.999 | -2896405.5349 | 1992.9108 | -2896.4055 | 739.4913 | -2896.4055 | 3515.8012 | 0.56684
[6 empty] | 1771476.228 | -3020437.884 | 506.17 | -45938722.2537 | -3020437.884 | 1771.4762 | -3020.4379 | 733.8231 | -3020.4379 | 3501.5958 | 0.50591
[6 empty] | 1550041.6995 | -3126258.9433 | 502.7635 | -45953791.9538 | -3126258.9433 | 1550.0417 | -3126.2589 | 728.9518 | -3126.2589 | 3489.4304 | 0.44421
[6 empty] | 1328607.171 | -3215467.3255 | 499.8737 | -45966844.8395 | -3215467.3255 | 1328.6072 | -3215.4673 | 724.8195 | -3215.4673 | 3479.1417 | 0.38188
[6 empty] | 1107172.6425 | -3289267.7315 | 497.4704 | -45977884.1427 | -3289267.7315 | 1107.1726 | -3289.2677 | 721.3827 | -3289.2677 | 3470.6071 | 0.31901
[6 empty] | 885738.114 | -3348569.8614 | 495.5308 | -45986912.5916 | -3348569.8614 | 885.7381 | -3348.5699 | 718.609 | -3348.5699 | 3463.7338 | 0.25572
[6 empty] | 664303.5855 | -3394053.2808 | 494.038 | -45993932.4137 | -3394053.2808 | 664.3036 | -3394.0533 | 716.4743 | -3394.0533 | 3458.453 | 0.19208
[6 empty] | 442869.057 | -3426210.5857 | 492.9798 | -45998945.3387 | -3426210.5857 | 442.8691 | -3426.2106 | 714.9611 | -3426.2106 | 3454.7145 | 0.12819
[6 empty] | 221434.5285 | -3445375.9521 | 492.3481 | -46001952.6006 | -3445375.9521 | 221.4345 | -3445.376 | 714.0578 | -3445.376 | 3452.4844 | 0.064138
[6 empty] | -5.2387e-10 | -3451743.2261 | 492.138 | -46002954.939 | -3451743.2261 | -5.2387e-13 | -3451.7432 | 713.7574 | -3451.7432 | 3451.7432 | -1.5177e-16
Note on B22: Autor: P_max no se da con reactiva 0 a la salida, por lo que el PF a la salida no es 1. La potencia es algo mayor que la rated porque la tension en bornas del stack de potencia es tb algo mayor
Note on B25: IF YES = '1' / NO = '0'

## V_0,98pu_DIG (hidden)
Inverter Voltage | 620 |  |  |  |  | P (W) | Q _Ii(VAr) | Vi_need | Q_Vdc (Var) | Q(Var) | P(kW) | Q_Ii(kVAr) | Vdc_min (V) | Q(kVAr) | S(kVA) | cos fi
Voltage operation pu | 0.98 |  |  | P_manual (kW), Q>0 | 3750 | 3750000 | 1607424.3747 | 648.8211 | 2236309.4846 | 1607424.3747 | 3750 | 1607.4244 | 937.8142 | 1607.4244 | 4079.9894 | 0.91912 | Capacitive
Line-Line Voltage (V) | 607.6 |  |  | P_manual (kW), Q<0 | 2846 | 2846000 | -2297050.7121 | 542.3621 | -47256790.8014 | -2297050.7121 | 2846 | -2297.0507 | 785.5778 | -2297.0507 | 3657.343 | 0.77816 | Inductive
Nm: Number of modules | 3 |  |  |  |  | 0 | 4352648.4912 | 714.2339 | 2519508.9012 | 2519508.9012 | 0 | 4352.6485 | 1031.3545 | 2519.5089 | 2519.5089 | 0
f(Hz) | 50 | wg(Hz) | 314.1593 |  |  | 221434.5285 | 4346411.37 | 714.0921 | 2518527.0194 | 2518527.0194 | 221.4345 | 4346.4114 | 1031.1517 | 2518.527 | 2528.2428 | 0.087584
Height (m) | 2700 |  |  |  |  | 442869.057 | 4327640.2939 | 713.6651 | 2515581.1425 | 2515581.1425 | 442.8691 | 4327.6403 | 1030.5411 | 2515.5811 | 2554.2673 | 0.17338
Temperature Max (ºC) ( TM) | 33 | TM_H_corrected(ºC) | 44.25 |  |  | 664303.5855 | 4296153.2302 | 712.9482 | 2510670.5749 | 2510670.5749 | 664.3036 | 4296.1532 | 1029.516 | 2510.6706 | 2597.0687 | 0.25579
Vdc_min (Tmax) | 951.5 | Vdc_min(sat) | 951.5 |  |  | 885738.114 | 4251636.8055 | 711.9335 | 2503794.1569 | 2503794.1569 | 885.7381 | 4251.6368 | 1028.0649 | 2503.7942 | 2655.8459 | 0.33351
TM_derating | 104.5% |  |  |  |  | 1107172.6425 | 4193630.0874 | 710.6092 | 2494950.2627 | 2494950.2627 | 1107.1726 | 4193.6301 | 1026.1711 | 2494.9503 | 2729.5802 | 0.40562
Vdc_min derating | 114.9% |  |  |  |  | 1328607.171 | 4121499.1158 | 708.9588 | 2484136.7988 | 2484136.7988 | 1328.6072 | 4121.4991 | 1023.8112 | 2484.1368 | 2817.1142 | 0.47162
Total derating@ TM | 120% |  |  |  |  | 1550041.6995 | 4034398.6625 | 706.9609 | 2471351.2013 | 2471351.2013 | 1550.0417 | 4034.3987 | 1020.9541 | 2471.3512 | 2917.2257 | 0.53134
Temperature Min (ºC) ( Tm) | -5 | Tm_H_corrected(ºC) | 6.25 |  |  | 1771476.228 | 3931215.2794 | 704.5867 | 2456590.4332 | 2456590.4332 | 1771.4762 | 3931.2153 | 1017.559 | 2456.5904 | 3028.6902 | 0.5849
Vdc_max (Tmin) | 1130 | Vdc_max(sat) | 1130 |  |  | 1992910.7564 | 3810481.4485 | 701.7986 | 2439850.9803 | 2439850.9803 | 1992.9108 | 3810.4814 | 1013.5719 | 2439.851 | 3150.3279 | 0.6326
Tm_derating | 111.6% |  |  |  |  | 2214345.2849 | 3670242.7053 | 698.5459 | 2421128.8474 | 2421128.8474 | 2214.3453 | 3670.2427 | 1008.9207 | 2421.1288 | 3281.0349 | 0.67489
Vdc_derating(V) | 106% |  |  |  |  | 2435779.8134 | 3507843.7204 | 694.7603 | 2400419.5532 | 2400419.5532 | 2435.7798 | 3507.8437 | 1003.5073 | 2400.4196 | 3419.8008 | 0.71226
Total derating@ Tm | 118.3% |  |  |  |  | 2657214.3419 | 3319565.0011 | 690.3455 | 2377718.1253 | 2377718.1253 | 2657.2143 | 3319.565 | 997.194 | 2377.7181 | 3565.7161 | 0.74521
[6 empty] | 2878648.8704 | 3099960.0934 | 685.1601 | 2353019.0935 | 2353019.0935 | 2878.6489 | 3099.9601 | 989.779 | 2353.0191 | 3717.9723 | 0.77425
Derating factor for TM | 118.3% |  |  |  |  | 3100083.3989 | 2840521.9452 | 678.9832 | 2326316.4838 | 2326316.4838 | 3100.0834 | 2840.5219 | 980.946 | 2326.3165 | 3875.8567 | 0.79984
[6 empty] | 3321517.9274 | 2526593.0797 | 671.433 | 2297603.8106 | 2297603.8106 | 3321.5179 | 2526.5931 | 970.1491 | 2297.6038 | 4038.7454 | 0.82241
Vi_max (V) | 658.3916 |  |  |  |  | 3542952.4559 | 2128415.3615 | 661.7325 | 2266874.0688 | 2128415.3615 | 3542.9525 | 2128.4154 | 956.2775 | 2128.4154 | 4133.118 | 0.85721
Ii (A) | 1242.32 |  |  |  |  | 3598311.088 | 2008599.1252 | 658.7856 | 2258875.5953 | 2008599.1252 | 3598.3111 | 2008.5991 | 952.0634 | 2008.5991 | 4120.9602 | 0.87317
P_max (W) (kW) | 3945560.6895 | P_base (kW) | 3945.5607 |  |  | 3653669.7202 | 1876884.1496 | 655.5307 | 2250750.4639 | 1876884.1496 | 3653.6697 | 1876.8841 | 947.4089 | 1876.8841 | 4107.5536 | 0.8895
Prated (W) | 3922230.6057 | Prated (kW) | 3922.2306 |  |  | 3709028.3523 | 1729688.7383 | 651.8741 | 2242498.5496 | 1729688.7383 | 3709.0284 | 1729.6887 | 942.1799 | 1729.6887 | 4092.5193 | 0.90629
[6 empty] | 3764386.9844 | 1561043.9782 | 647.6592 | 2234119.7252 | 1561043.9782 | 3764.387 | 1561.044 | 936.1527 | 1561.044 | 4075.2261 | 0.92372
GPTech Inverter | 1 |  |  |  |  | 3819745.6165 | 1359483.8666 | 642.5854 | 2225613.8614 | 1359483.8666 | 3819.7456 | 1359.4839 | 928.8972 | 1359.4839 | 4054.4609 | 0.94211
Inverter output current (A) | 1250 |  |  |  |  | 3875104.2486 | 1096240.4 | 635.898 | 2216980.8268 | 1096240.4 | 3875.1042 | 1096.2404 | 919.3341 | 1096.2404 | 4027.1797 | 0.96224
[6 empty] | 3930462.8808 | 582661.6754 | 622.6443 | 2208220.4879 | 582661.6754 | 3930.4629 | 582.6617 | 900.3813 | 582.6617 | 3973.4158 | 0.98919
Set Point Calculation Tool (@Tmax) | [5 empty] | 3985821.5129 | 418770.1386 | 618.5912 | 2199332.7088 | 418770.1386 | 3985.8215 | 418.7701 | 894.5854 | 418.7701 | 4007.7602 | 0.99453
P | 2846 | 2846 |  |  |  | 4041180.145 | 418770.1386 | 618.8462 | 2190317.3518 | 418770.1386 | 4041.1801 | 418.7701 | 894.95 | 418.7701 | 4062.8199 | 0.99467
| Q_ind_lim | -2297.0507 |  |  |  | 4096538.7771 | 418770.1386 | 619.1046 | 2181174.2767 | 418770.1386 | 4096.5388 | 418.7701 | 895.3196 | 418.7701 | 4117.8876 | 0.99482
| Q_cap_lim | 2356.7866 |  |  |  | 4151897.4093 | 418770.1386 | 619.3664 | 2171903.3412 | 418770.1386 | 4151.8974 | 418.7701 | 895.694 | 418.7701 | 4172.963 | 0.99495
Q | 0 | 0 |  |  |  | 4207256.0414 | 418770.1386 | 619.6316 | 2162504.4009 | 418770.1386 | 4207.256 | 418.7701 | 896.0732 | 418.7701 | 4228.0459 | 0.99508
PF | 1 | Io(P,Q) (A) | 2704.3102 |  |  | 4262614.6735 | 418770.1386 | 619.9002 | 2152977.309 | 418770.1386 | 4262.6147 | 418.7701 | 896.4573 | 418.7701 | 4283.1358 | 0.99521
Vdc_min(V) | 872.3372 |  |  |  |  | 4317973.3056 | 418770.1386 | 620.1722 | 2143321.9166 | 418770.1386 | 4317.9733 | 418.7701 | 896.8463 | 418.7701 | 4338.2326 | 0.99533
Vac_max(V) | 603.033 |  |  |  |  | 4373331.9378 | 418770.1386 | 620.4476 | 2133538.0726 | 418770.1386 | 4373.3319 | 418.7701 | 897.2401 | 418.7701 | 4393.3359 | 0.99545
[6 empty] | 4428690.5699 | 418770.1386 | 620.7264 | 2123625.6234 | 418770.1386 | 4428.6906 | 418.7701 | 897.6388 | 418.7701 | 4448.4456 | 0.99556
[6 empty] | 4373331.9378 | 418770.1386 | 620.4476 | -47033542.3135 | 418770.1386 | 4373.3319 | 418.7701 | 897.2401 | 418.7701 | 4393.3359 | 0.99545
[6 empty] | 4317973.3056 | 418770.1386 | 620.1722 | -47043326.1576 | 418770.1386 | 4317.9733 | 418.7701 | 896.8463 | 418.7701 | 4338.2326 | 0.99533
[6 empty] | 4262614.6735 | 418770.1386 | 619.9002 | -47052981.5499 | 418770.1386 | 4262.6147 | 418.7701 | 896.4573 | 418.7701 | 4283.1358 | 0.99521
[6 empty] | 4207256.0414 | 418770.1386 | 619.6316 | -47062508.6418 | 418770.1386 | 4207.256 | 418.7701 | 896.0732 | 418.7701 | 4228.0459 | 0.99508
[6 empty] | 4151897.4093 | 418770.1386 | 619.3664 | -47071907.5822 | 418770.1386 | 4151.8974 | 418.7701 | 895.694 | 418.7701 | 4172.963 | 0.99495
[6 empty] | 4096538.7771 | 418770.1386 | 619.1046 | -47081178.5177 | 418770.1386 | 4096.5388 | 418.7701 | 895.3196 | 418.7701 | 4117.8876 | 0.99482
[6 empty] | 4041180.145 | 418770.1386 | 618.8462 | -47090321.5928 | 418770.1386 | 4041.1801 | 418.7701 | 894.95 | 418.7701 | 4062.8199 | 0.99467
[6 empty] | 3985821.5129 | 418770.1386 | 618.5912 | -47099336.9498 | 418770.1386 | 3985.8215 | 418.7701 | 894.5854 | 418.7701 | 4007.7602 | 0.99453
[6 empty] | 3930462.8808 | 254878.6018 | 614.0358 | -47108224.7289 | 254878.6018 | 3930.4629 | 254.8786 | 888.0712 | 254.8786 | 3938.7183 | 0.9979
[6 empty] | 3875104.2486 | -258700.1228 | 600.2996 | -47116985.0678 | -258700.1228 | 3875.1042 | -258.7001 | 868.4284 | -258.7001 | 3883.73 | 0.99778
[6 empty] | 3819745.6165 | -521943.5894 | 593.1356 | -47125618.1024 | -521943.5894 | 3819.7456 | -521.9436 | 858.1838 | -521.9436 | 3855.2408 | 0.99079
[6 empty] | 3764386.9844 | -723503.701 | 587.5912 | -47134123.9662 | -723503.701 | 3764.387 | -723.5037 | 850.2554 | -723.5037 | 3833.2841 | 0.98203
[6 empty] | 3709028.3523 | -892148.4611 | 582.9117 | -47142502.7906 | -892148.4611 | 3709.0284 | -892.1485 | 843.5637 | -892.1485 | 3814.8159 | 0.97227
[6 empty] | 3653669.7202 | -1039343.8724 | 578.7964 | -47150754.7049 | -1039343.8724 | 3653.6697 | -1039.3439 | 837.6789 | -1039.3439 | 3798.6232 | 0.96184
[6 empty] | 3598311.088 | -1171058.848 | 575.089 | -47158879.8363 | -1171058.848 | 3598.3111 | -1171.0588 | 832.3773 | -1171.0588 | 3784.0747 | 0.95091
[6 empty] | 3542952.4559 | -1290875.0843 | 571.6956 | -47166878.3098 | -1290875.0843 | 3542.9525 | -1290.8751 | 827.5248 | -1290.8751 | 3770.7918 | 0.93958
[6 empty] | 3321517.9274 | -1689052.8024 | 560.271 | -47197608.0515 | -1689052.8024 | 3321.5179 | -1689.0528 | 811.1876 | -1689.0528 | 3726.3093 | 0.89137
[6 empty] | 3100083.3989 | -2002981.668 | 551.0968 | -47226320.7248 | -2002981.668 | 3100.0834 | -2002.9817 | 798.0684 | -2002.9817 | 3690.8607 | 0.83994
[6 empty] | 2878648.8704 | -2262419.8162 | 543.398 | -47253023.3345 | -2262419.8162 | 2878.6489 | -2262.4198 | 787.0592 | -2262.4198 | 3661.3062 | 0.78624
[6 empty] | 2657214.3419 | -2482024.7238 | 536.7951 | -47277722.3662 | -2482024.7238 | 2657.2143 | -2482.0247 | 777.617 | -2482.0247 | 3636.1016 | 0.73079
[6 empty] | 2435779.8134 | -2670303.4431 | 531.0686 | -47300423.7942 | -2670303.4431 | 2435.7798 | -2670.3034 | 769.4282 | -2670.3034 | 3614.3525 | 0.67392
[6 empty] | 2214345.2849 | -2832702.4281 | 526.0793 | -47321133.0883 | -2832702.4281 | 2214.3453 | -2832.7024 | 762.2934 | -2832.7024 | 3595.4872 | 0.61587
[6 empty] | 1992910.7564 | -2972941.1713 | 521.7323 | -47339855.2213 | -2972941.1713 | 1992.9108 | -2972.9412 | 756.0773 | -2972.9412 | 3579.1162 | 0.55682
[6 empty] | 1771476.228 | -3093675.0021 | 517.9608 | -47356594.6742 | -3093675.0021 | 1771.4762 | -3093.675 | 750.6839 | -3093.675 | 3564.9619 | 0.49691
[6 empty] | 1550041.6995 | -3196858.3853 | 514.7156 | -47371355.4423 | -3196858.3853 | 1550.0417 | -3196.8584 | 746.0432 | -3196.8584 | 3552.8204 | 0.43628
[6 empty] | 1328607.171 | -3283958.8385 | 511.9602 | -47384141.0398 | -3283958.8385 | 1328.6072 | -3283.9588 | 742.103 | -3283.9588 | 3542.539 | 0.37504
[6 empty] | 1107172.6425 | -3356089.8101 | 509.667 | -47394954.5037 | -3356089.8101 | 1107.1726 | -3356.0898 | 738.8238 | -3356.0898 | 3534.002 | 0.31329
[6 empty] | 885738.114 | -3414096.5283 | 507.8154 | -47403798.3979 | -3414096.5283 | 885.7381 | -3414.0965 | 736.176 | -3414.0965 | 3527.1216 | 0.25112
[6 empty] | 664303.5855 | -3458612.953 | 506.3898 | -47410674.8159 | -3458612.953 | 664.3036 | -3458.613 | 734.1375 | -3458.613 | 3521.8323 | 0.18862
[6 empty] | 442869.057 | -3490100.0167 | 505.3791 | -47415585.3834 | -3490100.0167 | 442.8691 | -3490.1 | 732.6921 | -3490.1 | 3518.0863 | 0.12588
[6 empty] | 221434.5285 | -3508871.0928 | 504.7755 | -47418531.2604 | -3508871.0928 | 221.4345 | -3508.8711 | 731.829 | -3508.8711 | 3515.8512 | 0.062982
[6 empty] | -5.2387e-10 | -3515108.214 | 504.5748 | -47419513.1421 | -3515108.214 | -5.2387e-13 | -3515.1082 | 731.542 | -3515.1082 | 3515.1082 | -1.4903e-16
Note on B22: Autor: P_max no se da con reactiva 0 a la salida, por lo que el PF a la salida no es 1. La potencia es algo mayor que la rated porque la tension en bornas del stack de potencia es tb algo mayor
Note on B25: IF YES = '1' / NO = '0'

## V_1pu_DIG (hidden)
Inverter Voltage | 620 |  |  |  |  | P (W) | Q _Ii(VAr) | Vi_need | Q_Vdc (Var) | Q(Var) | P(kW) | Q_Ii(kVAr) | Vdc_min (V) | Q(kVAr) | S(kVA) | cos fi
Voltage operation pu | 1 |  |  | P_manual (kW), Q>0 | 3750 | 3750000 | 1868166.1256 | 666.4753 | 1825941.4535 | 1825941.4535 | 3750 | 1868.1661 | 963.0597 | 1825.9415 | 4170.9186 | 0.89908
Line-Line Voltage (V) | 620 |  |  | P_manual (kW), Q<0 | 2846 | 2846000 | -2394824.3571 | 552.9314 | -48695324.7009 | -2394824.3571 | 2846 | -2394.8244 | 800.6918 | -2394.8244 | 3719.5295 | 0.76515
Nm: Number of modules | 3 |  |  |  |  | 0 | 4450198.7965 | 726.6707 | 2103413.87 | 2103413.87 | 0 | 4450.1988 | 1049.1391 | 2103.4139 | 2103.4139 | 0
f(Hz) | 50 | wg(Hz) | 314.1593 |  |  | 221434.5285 | 4444086.6099 | 726.5341 | 2102451.6266 | 2102451.6266 | 221.4345 | 4444.0866 | 1048.9438 | 2102.4516 | 2114.0804 | 0.10474
Height (m) | 2700 |  |  |  |  | 442869.057 | 4425693.867 | 726.1229 | 2099564.6785 | 2099564.6785 | 442.8691 | 4425.6939 | 1048.3557 | 2099.5647 | 2145.7644 | 0.20639
Temperature Max (ºC) ( TM) | 33 | TM_H_corrected(ºC) | 44.25 |  |  | 664303.5855 | 4394849.4041 | 725.4327 | 2094752.371 | 2094752.371 | 664.3036 | 4394.8494 | 1047.3688 | 2094.7524 | 2197.5638 | 0.30229
Vdc_min (Tmax) | 951.5 | Vdc_min(sat) | 951.5 |  |  | 885738.114 | 4351258.9452 | 724.4563 | 2088013.6127 | 2088013.6127 | 885.7381 | 4351.2589 | 1045.9725 | 2088.0136 | 2268.1122 | 0.39052
TM_derating | 104.5% |  |  |  |  | 1107172.6425 | 4294490.5247 | 723.1827 | 2079346.8735 | 2079346.8735 | 1107.1726 | 4294.4905 | 1044.1512 | 2079.3469 | 2355.7408 | 0.46999
Vdc_min derating | 114.9% |  |  |  |  | 1328607.171 | 4223951.7057 | 721.5969 | 2068750.1833 | 2068750.1833 | 1328.6072 | 4223.9517 | 1041.8836 | 2068.7502 | 2458.6428 | 0.54038
Total derating@ TM | 120% |  |  |  |  | 1550041.6995 | 4138855.5921 | 719.6793 | 2056221.1297 | 2056221.1297 | 1550.0417 | 4138.8556 | 1039.1414 | 2056.2211 | 2575.0096 | 0.60196
Temperature Min (ºC) ( Tm) | -5 | Tm_H_corrected(ºC) | 6.25 |  |  | 1771476.228 | 4038170.6354 | 717.4038 | 2041756.8552 | 2041756.8552 | 1771.4762 | 4038.1706 | 1035.8874 | 2041.7569 | 2703.1276 | 0.65534
Vdc_max (Tmin) | 1130 | Vdc_max(sat) | 1130 |  |  | 1992910.7564 | 3920545.7775 | 714.7363 | 2025354.0537 | 2025354.0537 | 1992.9108 | 3920.5458 | 1032.0729 | 2025.3541 | 2841.4349 | 0.70137
Tm_derating | 111.6% |  |  |  |  | 2214345.2849 | 3784196.1367 | 711.6316 | 2007008.9672 | 2007008.9672 | 2214.3453 | 3784.1961 | 1027.6331 | 2007.009 | 2988.5465 | 0.74094
Vdc_derating(V) | 106% |  |  |  |  | 2435779.8134 | 3626722.0799 | 708.0289 | 1986717.3809 | 1986717.3809 | 2435.7798 | 3626.7221 | 1022.4813 | 1986.7174 | 3143.2577 | 0.77492
Total derating@ Tm | 118.3% |  |  |  |  | 2657214.3419 | 3444808.5837 | 703.8442 | 1964474.6187 | 1964474.6187 | 2657.2143 | 3444.8086 | 1016.4972 | 1964.4746 | 3304.5345 | 0.80411
[6 empty] | 2878648.8704 | 3233692.2849 | 698.9562 | 1940275.5378 | 1940275.5378 | 2878.6489 | 3233.6923 | 1009.5074 | 1940.2755 | 3471.4966 | 0.82922
Derating factor for TM | 118.3% |  |  |  |  | 3100083.3989 | 2986130.5722 | 693.1806 | 1914114.5223 | 1914114.5223 | 3100.0834 | 2986.1306 | 1001.2483 | 1914.1145 | 3643.3983 | 0.85088
[6 empty] | 3321517.9274 | 2690147.2101 | 686.2115 | 1885985.4768 | 1885985.4768 | 3321.5179 | 2690.1472 | 991.2824 | 1885.9855 | 3819.6103 | 0.8696
Vi_max (V) | 658.3916 |  |  |  |  | 3542952.4559 | 2323093.417 | 677.4694 | 1855881.8193 | 1855881.8193 | 3542.9525 | 2323.0934 | 978.7812 | 1855.8818 | 3999.6012 | 0.88583
Ii (A) | 1242.32 |  |  |  |  | 3598311.088 | 2215264.7239 | 674.8797 | 1848046.5535 | 1848046.5535 | 3598.3111 | 2215.2647 | 975.078 | 1848.0466 | 4045.1352 | 0.88954
P_max (W) (kW) | 4026082.3363 | P_base (kW) | 4026.0823 |  |  | 3653669.7202 | 2098622.7892 | 672.0672 | 1840087.3191 | 1840087.3191 | 3653.6697 | 2098.6228 | 971.0561 | 1840.0873 | 4090.8708 | 0.89313
Prated (W) | 4002276.1282 | Prated (kW) | 4002.2761 |  |  | 3709028.3523 | 1971159.9782 | 668.9802 | 1832003.9987 | 1832003.9987 | 3709.0284 | 1971.16 | 966.6416 | 1832.004 | 4136.8019 | 0.89659
[6 empty] | 3764386.9844 | 1829910.8996 | 665.5425 | 1823796.473 | 1823796.473 | 3764.387 | 1829.9109 | 961.7258 | 1823.7965 | 4182.9228 | 0.89994
GPTech Inverter | 1 |  |  |  |  | 3819745.6165 | 1670150.9224 | 661.6329 | 1815464.6205 | 1670150.9224 | 3819.7456 | 1670.1509 | 956.135 | 1670.1509 | 4168.916 | 0.91624
Inverter output current (A) | 1250 |  |  |  |  | 3875104.2486 | 1483443.6695 | 657.0343 | 1807008.3178 | 1483443.6695 | 3875.1042 | 1483.4437 | 949.5591 | 1483.4437 | 4149.3419 | 0.93391
[6 empty] | 3930462.8808 | 1251484.7995 | 651.2759 | 1798427.4395 | 1251484.7995 | 3930.4629 | 1251.4848 | 941.3246 | 1251.4848 | 4124.8943 | 0.95286
Set Point Calculation Tool (@Tmax) | [5 empty] | 3985821.5129 | 912188.5453 | 642.76 | 1789721.8581 | 912188.5453 | 3985.8215 | 912.1885 | 929.1469 | 912.1885 | 4088.8704 | 0.9748
P | 2846 | 2846 |  |  |  | 4041180.145 | 436037.2122 | 630.733 | 1780891.4443 | 436037.2122 | 4041.1801 | 436.0372 | 911.9482 | 436.0372 | 4064.636 | 0.99423
| Q_ind_lim | -2394.8244 |  |  |  | 4096538.7771 | 436037.2122 | 630.9765 | 1771936.0665 | 436037.2122 | 4096.5388 | 436.0372 | 912.2964 | 436.0372 | 4119.6794 | 0.99438
| Q_cap_lim | 1943.9667 |  |  |  | 4151897.4093 | 436037.2122 | 631.2232 | 1762855.5911 | 436037.2122 | 4151.8974 | 436.0372 | 912.6492 | 436.0372 | 4174.7312 | 0.99453
Q | 0 | 0 |  |  |  | 4207256.0414 | 436037.2122 | 631.4732 | 1753649.8825 | 436037.2122 | 4207.256 | 436.0372 | 913.0066 | 436.0372 | 4229.791 | 0.99467
PF | 1 | Io(P,Q) (A) | 2650.224 |  |  | 4262614.6735 | 436037.2122 | 631.7263 | 1744318.8031 | 436037.2122 | 4262.6147 | 436.0372 | 913.3686 | 436.0372 | 4284.8585 | 0.99481
Vdc_min(V) | 889.3955 |  |  |  |  | 4317973.3056 | 436037.2122 | 631.9827 | 1734862.2131 | 436037.2122 | 4317.9733 | 436.0372 | 913.7352 | 436.0372 | 4339.9334 | 0.99494
Vac_max(V) | 614.9619 |  |  |  |  | 4373331.9378 | 436037.2122 | 632.2422 | 1725279.9707 | 436037.2122 | 4373.3319 | 436.0372 | 914.1064 | 436.0372 | 4395.0154 | 0.99507
[6 empty] | 4428690.5699 | 436037.2122 | 632.505 | 1715571.9318 | 436037.2122 | 4428.6906 | 436.0372 | 914.4821 | 436.0372 | 4450.1043 | 0.99519
[6 empty] | 4373331.9378 | 436037.2122 | 632.2422 | -48476637.9892 | 436037.2122 | 4373.3319 | 436.0372 | 914.1064 | 436.0372 | 4395.0154 | 0.99507
[6 empty] | 4317973.3056 | 436037.2122 | 631.9827 | -48486220.2316 | 436037.2122 | 4317.9733 | 436.0372 | 913.7352 | 436.0372 | 4339.9334 | 0.99494
[6 empty] | 4262614.6735 | 436037.2122 | 631.7263 | -48495676.8216 | 436037.2122 | 4262.6147 | 436.0372 | 913.3686 | 436.0372 | 4284.8585 | 0.99481
[6 empty] | 4207256.0414 | 436037.2122 | 631.4732 | -48505007.901 | 436037.2122 | 4207.256 | 436.0372 | 913.0066 | 436.0372 | 4229.791 | 0.99467
[6 empty] | 4151897.4093 | 436037.2122 | 631.2232 | -48514213.6096 | 436037.2122 | 4151.8974 | 436.0372 | 912.6492 | 436.0372 | 4174.7312 | 0.99453
[6 empty] | 4096538.7771 | 436037.2122 | 630.9765 | -48523294.085 | 436037.2122 | 4096.5388 | 436.0372 | 912.2964 | 436.0372 | 4119.6794 | 0.99438
[6 empty] | 4041180.145 | 436037.2122 | 630.733 | -48532249.4628 | 436037.2122 | 4041.1801 | 436.0372 | 911.9482 | 436.0372 | 4064.636 | 0.99423
[6 empty] | 3985821.5129 | -40114.1209 | 618.2321 | -48541079.8766 | -40114.1209 | 3985.8215 | -40.1141 | 894.0719 | -40.1141 | 3986.0234 | 0.99995
[6 empty] | 3930462.8808 | -379410.375 | 609.2545 | -48549785.458 | -379410.375 | 3930.4629 | -379.4104 | 881.2339 | -379.4104 | 3948.7328 | 0.99537
[6 empty] | 3875104.2486 | -611369.2451 | 603.0401 | -48558366.3363 | -611369.2451 | 3875.1042 | -611.3692 | 872.3473 | -611.3692 | 3923.0352 | 0.98778
[6 empty] | 3819745.6165 | -798076.498 | 597.9911 | -48566822.639 | -798076.498 | 3819.7456 | -798.0765 | 865.1272 | -798.0765 | 3902.2279 | 0.97886
[6 empty] | 3764386.9844 | -957836.4752 | 593.6367 | -48575154.4915 | -957836.4752 | 3764.387 | -957.8365 | 858.9005 | -957.8365 | 3884.3352 | 0.96912
[6 empty] | 3709028.3523 | -1099085.5538 | 589.7601 | -48583362.0172 | -1099085.5538 | 3709.0284 | -1099.0856 | 853.3569 | -1099.0856 | 3868.4468 | 0.95879
[6 empty] | 3653669.7202 | -1226548.3647 | 586.2398 | -48591445.3376 | -1226548.3647 | 3653.6697 | -1226.5484 | 848.3229 | -1226.5484 | 3854.0528 | 0.94801
[6 empty] | 3598311.088 | -1343190.2995 | 582.9998 | -48599404.572 | -1343190.2995 | 3598.3111 | -1343.1903 | 843.6897 | -1343.1903 | 3840.8336 | 0.93686
[6 empty] | 3542952.4559 | -1451018.9925 | 579.9885 | -48607239.8378 | -1451018.9925 | 3542.9525 | -1451.019 | 839.3835 | -1451.019 | 3828.5726 | 0.9254
[6 empty] | 3321517.9274 | -1818072.7857 | 569.6185 | -48637343.4953 | -1818072.7857 | 3321.5179 | -1818.0728 | 824.5544 | -1818.0728 | 3786.538 | 0.87719
[6 empty] | 3100083.3989 | -2114056.1477 | 561.1168 | -48665472.5408 | -2114056.1477 | 3100.0834 | -2114.0561 | 812.397 | -2114.0561 | 3752.2994 | 0.82618
[6 empty] | 2878648.8704 | -2361617.8604 | 553.9058 | -48691633.5563 | -2361617.8604 | 2878.6489 | -2361.6179 | 802.0852 | -2361.6179 | 3723.4202 | 0.77312
[6 empty] | 2657214.3419 | -2572734.1592 | 547.6813 | -48715832.6372 | -2572734.1592 | 2657.2143 | -2572.7342 | 793.1843 | -2572.7342 | 3698.6145 | 0.71844
[6 empty] | 2435779.8134 | -2754647.6555 | 542.2605 | -48738075.3994 | -2754647.6555 | 2435.7798 | -2754.6477 | 785.4326 | -2754.6477 | 3677.1058 | 0.66242
[6 empty] | 2214345.2849 | -2912121.7123 | 537.5239 | -48758366.9857 | -2912121.7123 | 2214.3453 | -2912.1217 | 778.6592 | -2912.1217 | 3658.3846 | 0.60528
[6 empty] | 1992910.7564 | -3048471.3531 | 533.3887 | -48776712.0722 | -3048471.3531 | 1992.9108 | -3048.4714 | 772.7458 | -3048.4714 | 3642.097 | 0.54719
[6 empty] | 1771476.228 | -3166096.211 | 529.7954 | -48793114.8737 | -3166096.211 | 1771.4762 | -3166.0962 | 767.6075 | -3166.0962 | 3627.9875 | 0.48828
[6 empty] | 1550041.6995 | -3266781.1677 | 526.7002 | -48807579.1482 | -3266781.1677 | 1550.0417 | -3266.7812 | 763.1813 | -3266.7812 | 3615.8662 | 0.42868
[6 empty] | 1328607.171 | -3351877.2813 | 524.0699 | -48820108.2018 | -3351877.2813 | 1328.6072 | -3351.8773 | 759.42 | -3351.8773 | 3605.5899 | 0.36849
[6 empty] | 1107172.6425 | -3422416.1002 | 521.8795 | -48830704.892 | -3422416.1002 | 1107.1726 | -3422.4161 | 756.2878 | -3422.4161 | 3597.0492 | 0.3078
[6 empty] | 885738.114 | -3479184.5207 | 520.1101 | -48839371.6312 | -3479184.5207 | 885.7381 | -3479.1845 | 753.7574 | -3479.1845 | 3590.1611 | 0.24671
[6 empty] | 664303.5855 | -3522774.9797 | 518.7473 | -48846110.3895 | -3522774.9797 | 664.3036 | -3522.775 | 751.8086 | -3522.775 | 3584.863 | 0.18531
[6 empty] | 442869.057 | -3553619.4426 | 517.7808 | -48850922.697 | -3553619.4426 | 442.8691 | -3553.6194 | 750.4265 | -3553.6194 | 3581.1093 | 0.12367
[6 empty] | 221434.5285 | -3572012.1855 | 517.2036 | -48853809.6451 | -3572012.1855 | 221.4345 | -3572.0122 | 749.6012 | -3572.0122 | 3578.8691 | 0.061873
[6 empty] | -5.2387e-10 | -3578124.3721 | 517.0117 | -48854771.8885 | -3578124.3721 | -5.2387e-13 | -3578.1244 | 749.3267 | -3578.1244 | 3578.1244 | -1.4641e-16
Note on B22: Autor: P_max no se da con reactiva 0 a la salida, por lo que el PF a la salida no es 1. La potencia es algo mayor que la rated porque la tension en bornas del stack de potencia es tb algo mayor
Note on B25: IF YES = '1' / NO = '0'

## V_1,02pu_DIG (hidden)
Inverter Voltage | 620 |  |  |  |  | P (W) | Q _Ii(VAr) | Vi_need | Q_Vdc (Var) | Q(Var) | P(kW) | Q_Ii(kVAr) | Vdc_min (V) | Q(kVAr) | S(kVA) | cos fi
Voltage operation pu | 1.02 |  |  | P_manual (kW), Q>0 | 3750 | 3750000 | 2097422.6709 | 683.1437 | 1396644.6415 | 1396644.6415 | 3750 | 2097.4227 | 986.8955 | 1396.6446 | 4001.6392 | 0.93712 | Capacitive
Line-Line Voltage (V) | 632.4 |  |  | P_manual (kW), Q<0 | 2846 | 2846000 | -2489943.7235 | 563.6433 | -50152429.5141 | -2489943.7235 | 2846 | -2489.9437 | 816.0099 | -2489.9437 | 3781.4727 | 0.75262 | Inductive
Nm: Number of modules | 3 |  |  |  |  | 0 | 4548097.9315 | 739.1076 | 1668618.2956 | 1668618.2956 | 0 | 4548.0979 | 1066.9238 | 1668.6183 | 1668.6183 | 0
f(Hz) | 50 | wg(Hz) | 314.1593 |  |  | 221434.5285 | 4542105.7692 | 738.9759 | 1667674.9205 | 1667674.9205 | 221.4345 | 4542.1058 | 1066.7355 | 1667.6749 | 1682.3118 | 0.13163
Height (m) | 2700 |  |  |  |  | 442869.057 | 4524076.3552 | 738.5796 | 1664844.5895 | 1664844.5895 | 442.8691 | 4524.0764 | 1066.1688 | 1664.8446 | 1722.7421 | 0.25707
Temperature Max (ºC) ( TM) | 33 | TM_H_corrected(ºC) | 44.25 |  |  | 664303.5855 | 4493848.5437 | 737.9146 | 1660126.686 | 1660126.686 | 664.3036 | 4493.8485 | 1065.2179 | 1660.1267 | 1788.1051 | 0.37151
Vdc_min (Tmax) | 951.5 | Vdc_min(sat) | 951.5 |  |  | 885738.114 | 4451145.6227 | 736.9743 | 1653520.1814 | 1653520.1814 | 885.7381 | 4451.1456 | 1063.8732 | 1653.5202 | 1875.8094 | 0.47219
TM_derating | 104.5% |  |  |  |  | 1107172.6425 | 4395562.1824 | 735.7485 | 1645023.6341 | 1645023.6341 | 1107.1726 | 4395.5622 | 1062.1203 | 1645.0236 | 1982.9105 | 0.55836
Vdc_min derating | 114.9% |  |  |  |  | 1328607.171 | 4326543.6816 | 734.2235 | 1634635.1879 | 1634635.1879 | 1328.6072 | 4326.5437 | 1059.9396 | 1634.6352 | 2106.4732 | 0.63073
Total derating@ TM | 120% |  |  |  |  | 1550041.6995 | 4243356.1489 | 732.3813 | 1622352.57 | 1622352.57 | 1550.0417 | 4243.3561 | 1057.3053 | 1622.3526 | 2243.8042 | 0.69081
Temperature Min (ºC) ( Tm) | -5 | Tm_H_corrected(ºC) | 6.25 |  |  | 1771476.228 | 4145041.7872 | 730.1981 | 1608173.0886 | 1608173.0886 | 1771.4762 | 4145.0418 | 1054.1833 | 1608.1731 | 2392.5611 | 0.74041
Vdc_max (Tmin) | 1130 | Vdc_max(sat) | 1130 |  |  | 1992910.7564 | 4030353.42 | 727.643 | 1592093.6296 | 1592093.6296 | 1992.9108 | 4030.3534 | 1050.5295 | 1592.0936 | 2550.7755 | 0.7813
Tm_derating | 111.6% |  |  |  |  | 2214345.2849 | 3897655.6286 | 724.6754 | 1574110.6536 | 1574110.6536 | 2214.3453 | 3897.6556 | 1046.2859 | 1574.1107 | 2716.8271 | 0.81505
Vdc_derating(V) | 106% |  |  |  |  | 2435779.8134 | 3744770.7147 | 721.2413 | 1554220.1917 | 1554220.1917 | 2435.7798 | 3744.7707 | 1041.375 | 1554.2202 | 2889.3985 | 0.84301
Total derating@ Tm | 118.3% |  |  |  |  | 2657214.3419 | 3568727.8004 | 717.2666 | 1532417.8411 | 1532417.8411 | 2657.2143 | 3568.7278 | 1035.6912 | 1532.4178 | 3067.4244 | 0.86627
[6 empty] | 2878648.8704 | 3365329.4423 | 712.6466 | 1508698.7603 | 1508698.7603 | 2878.6489 | 3365.3294 | 1029.0847 | 1508.6988 | 3250.0448 | 0.88573
Derating factor for TM | 118.3% |  |  |  |  | 3100083.3989 | 3128342.1201 | 707.2257 | 1483057.6634 | 1483057.6634 | 3100.0834 | 3128.3421 | 1021.3328 | 1483.0577 | 3436.5647 | 0.90209
[6 empty] | 3321517.9274 | 2847812.0512 | 700.7546 | 1455488.8146 | 1455488.8146 | 3321.5179 | 2847.8121 | 1012.079 | 1455.4888 | 3626.421 | 0.91592
Vi_max (V) | 658.3916 |  |  |  |  | 3542952.4559 | 2505960.6574 | 692.7872 | 1425986.0211 | 1425986.0211 | 3542.9525 | 2505.9607 | 1000.6857 | 1425.986 | 3819.1554 | 0.92768
Ii (A) | 1242.32 |  |  |  |  | 3598311.088 | 2407274.2827 | 690.47 | 1418307.3741 | 1418307.3741 | 3598.3111 | 2407.2743 | 997.3721 | 1418.3074 | 3867.7433 | 0.93034
P_max (W) (kW) | 4106603.983 | P_base (kW) | 4106.604 |  |  | 3653669.7202 | 2301672.5762 | 687.9819 | 1410507.3333 | 1410507.3333 | 3653.6697 | 2301.6726 | 993.8141 | 1410.5073 | 3916.4823 | 0.9329
Prated (W) | 4082321.6508 | Prated (kW) | 4082.3217 |  |  | 3709028.3523 | 2187892.7279 | 685.2909 | 1402585.7881 | 1402585.7881 | 3709.0284 | 2187.8927 | 989.966 | 1402.5858 | 3965.3673 | 0.93536
[6 empty] | 3764386.9844 | 2064202.3954 | 682.3535 | 1394542.6264 | 1394542.6264 | 3764.387 | 2064.2024 | 985.7656 | 1394.5426 | 4014.3939 | 0.93772
GPTech Inverter | 1 |  |  |  |  | 3819745.6165 | 1928109.5497 | 679.1069 | 1386377.7339 | 1386377.7339 | 3819.7456 | 1928.1095 | 981.1229 | 1386.3777 | 4063.5575 | 0.94
Inverter output current (A) | 1250 |  |  |  |  | 3875104.2486 | 1775789.8003 | 675.4547 | 1378090.9947 | 1378090.9947 | 3875.1042 | 1775.7898 | 975.9003 | 1378.091 | 4112.854 | 0.94219
[6 empty] | 3930462.8808 | 1600797.3497 | 671.2344 | 1369682.2908 | 1369682.2908 | 3930.4629 | 1600.7973 | 969.8651 | 1369.6823 | 4162.2792 | 0.94431
Set Point Calculation Tool (@Tmax) | [5 empty] | 3985821.5129 | 1390512.3464 | 666.1275 | 1361151.5024 | 1361151.5024 | 3985.8215 | 1390.5123 | 962.5623 | 1361.1515 | 4211.8294 | 0.94634
P | 2846 | 2846 |  |  |  | 4041180.145 | 1111939.8209 | 659.3012 | 1352498.5078 | 1111939.8209 | 4041.1801 | 1111.9398 | 952.8008 | 1111.9398 | 4191.3658 | 0.96417
| Q_ind_lim | -2489.9437 |  |  |  | 4096538.7771 | 453653.1156 | 642.8912 | 1343723.1835 | 453653.1156 | 4096.5388 | 453.6531 | 929.3344 | 453.6531 | 4121.5811 | 0.99392
| Q_cap_lim | 1512.3166 |  |  |  | 4151897.4093 | 453653.1156 | 643.1239 | 1334825.4038 | 453653.1156 | 4151.8974 | 453.6531 | 929.6672 | 453.6531 | 4176.6079 | 0.99408
Q | 0 | 0 |  |  |  | 4207256.0414 | 453653.1156 | 643.3597 | 1325805.0413 | 453653.1156 | 4207.256 | 453.6531 | 930.0044 | 453.6531 | 4231.6432 | 0.99424
PF | 1 | Io(P,Q) (A) | 2598.2588 |  |  | 4262614.6735 | 453653.1156 | 643.5985 | 1316661.9666 | 453653.1156 | 4262.6147 | 453.6531 | 930.3459 | 453.6531 | 4286.6869 | 0.99438
Vdc_min(V) | 906.4844 |  |  |  |  | 4317973.3056 | 453653.1156 | 643.8404 | 1307396.0484 | 453653.1156 | 4317.9733 | 453.6531 | 930.6918 | 453.6531 | 4341.7387 | 0.99453
Vac_max(V) | 626.9122 |  |  |  |  | 4373331.9378 | 453653.1156 | 644.0853 | 1298007.1534 | 453653.1156 | 4373.3319 | 453.6531 | 931.042 | 453.6531 | 4396.7981 | 0.99466
[6 empty] | 4428690.5699 | 453653.1156 | 644.3332 | 1288495.1463 | 453653.1156 | 4428.6906 | 453.6531 | 931.3965 | 453.6531 | 4451.8649 | 0.99479
[6 empty] | 4373331.9378 | 453653.1156 | 644.0853 | -49938120.0359 | 453653.1156 | 4373.3319 | 453.6531 | 931.042 | 453.6531 | 4396.7981 | 0.99466
[6 empty] | 4317973.3056 | 453653.1156 | 643.8404 | -49947508.9309 | 453653.1156 | 4317.9733 | 453.6531 | 930.6918 | 453.6531 | 4341.7387 | 0.99453
[6 empty] | 4262614.6735 | 453653.1156 | 643.5985 | -49956774.849 | 453653.1156 | 4262.6147 | 453.6531 | 930.3459 | 453.6531 | 4286.6869 | 0.99438
[6 empty] | 4207256.0414 | 453653.1156 | 643.3597 | -49965917.9237 | 453653.1156 | 4207.256 | 453.6531 | 930.0044 | 453.6531 | 4231.6432 | 0.99424
[6 empty] | 4151897.4093 | 453653.1156 | 643.1239 | -49974938.2862 | 453653.1156 | 4151.8974 | 453.6531 | 929.6672 | 453.6531 | 4176.6079 | 0.99408
[6 empty] | 4096538.7771 | 453653.1156 | 642.8912 | -49983836.0659 | 453653.1156 | 4096.5388 | 453.6531 | 929.3344 | 453.6531 | 4121.5811 | 0.99392
[6 empty] | 4041180.145 | -204633.5898 | 626.0332 | -49992611.3903 | -204633.5898 | 4041.1801 | -204.6336 | 905.2275 | -204.6336 | 4046.3579 | 0.99872
[6 empty] | 3985821.5129 | -483206.1152 | 618.7648 | -50001264.3849 | -483206.1152 | 3985.8215 | -483.2061 | 894.8337 | -483.2061 | 4015.0045 | 0.99273
[6 empty] | 3930462.8808 | -693491.1185 | 613.2211 | -50009795.1733 | -693491.1185 | 3930.4629 | -693.4911 | 886.9062 | -693.4911 | 3991.1738 | 0.98479
[6 empty] | 3875104.2486 | -868483.5691 | 608.5693 | -50018203.8772 | -868483.5691 | 3875.1042 | -868.4836 | 880.2541 | -868.4836 | 3971.2336 | 0.97579
[6 empty] | 3819745.6165 | -1020803.3185 | 604.4911 | -50026490.6164 | -1020803.3185 | 3819.7456 | -1020.8033 | 874.4222 | -1020.8033 | 3953.7951 | 0.9661
[6 empty] | 3764386.9844 | -1156896.1642 | 600.8239 | -50034655.5088 | -1156896.1642 | 3764.387 | -1156.8962 | 869.1781 | -1156.8962 | 3938.1491 | 0.95588
[6 empty] | 3709028.3523 | -1280586.4967 | 597.4714 | -50042698.6706 | -1280586.4967 | 3709.0284 | -1280.5865 | 864.3841 | -1280.5865 | 3923.8748 | 0.94525
[6 empty] | 3653669.7202 | -1394366.3451 | 594.3708 | -50050620.2157 | -1394366.3451 | 3653.6697 | -1394.3663 | 859.9502 | -1394.3663 | 3910.6981 | 0.93428
[6 empty] | 3598311.088 | -1499968.0516 | 591.4785 | -50058420.2566 | -1499968.0516 | 3598.3111 | -1499.9681 | 855.8143 | -1499.9681 | 3898.4288 | 0.92302
[6 empty] | 3542952.4559 | -1598654.4262 | 588.7628 | -50066098.9036 | -1598654.4262 | 3542.9525 | -1598.6544 | 851.9308 | -1598.6544 | 3886.9278 | 0.9115
[6 empty] | 3321517.9274 | -1940505.82 | 579.2571 | -50095601.697 | -1940505.82 | 3321.5179 | -1940.5058 | 838.3376 | -1940.5058 | 3846.8226 | 0.86344
[6 empty] | 3100083.3989 | -2221035.8889 | 571.3383 | -50123170.5459 | -2221035.8889 | 3100.0834 | -2221.0359 | 827.0138 | -2221.0359 | 3813.5964 | 0.8129
[6 empty] | 2878648.8704 | -2458023.2112 | 564.5622 | -50148811.6427 | -2458023.2112 | 2878.6489 | -2458.0232 | 817.3239 | -2458.0232 | 3785.3002 | 0.76048
[6 empty] | 2657214.3419 | -2661421.5692 | 558.6809 | -50172530.7235 | -2661421.5692 | 2657.2143 | -2661.4216 | 808.9137 | -2661.4216 | 3760.8447 | 0.70655
[6 empty] | 2435779.8134 | -2837464.4836 | 553.5402 | -50194333.0742 | -2837464.4836 | 2435.7798 | -2837.4645 | 801.5624 | -2837.4645 | 3739.5492 | 0.65136
[6 empty] | 2214345.2849 | -2990349.3975 | 549.0366 | -50214223.5361 | -2990349.3975 | 2214.3453 | -2990.3494 | 795.1224 | -2990.3494 | 3720.9561 | 0.5951
[6 empty] | 1992910.7564 | -3123047.1889 | 545.0976 | -50232206.5121 | -3123047.1889 | 1992.9108 | -3123.0472 | 789.4895 | -3123.0472 | 3704.7425 | 0.53794
[6 empty] | 1771476.228 | -3237735.556 | 541.67 | -50248285.971 | -3237735.556 | 1771.4762 | -3237.7356 | 784.5882 | -3237.7356 | 3690.672 | 0.47999
[6 empty] | 1550041.6995 | -3336049.9178 | 538.7145 | -50262465.4525 | -3336049.9178 | 1550.0417 | -3336.0499 | 780.3617 | -3336.0499 | 3678.5674 | 0.42137
[6 empty] | 1328607.171 | -3419237.4504 | 536.201 | -50274748.0703 | -3419237.4504 | 1328.6072 | -3419.2375 | 776.7674 | -3419.2375 | 3668.2941 | 0.36219
[6 empty] | 1107172.6425 | -3488255.9512 | 534.1066 | -50285136.5165 | -3488255.9512 | 1107.1726 | -3488.256 | 773.7724 | -3488.256 | 3659.7487 | 0.30253
[6 empty] | 885738.114 | -3543839.3915 | 532.4139 | -50293633.0638 | -3543839.3915 | 885.7381 | -3543.8394 | 771.3519 | -3543.8394 | 3652.8523 | 0.24248
[6 empty] | 664303.5855 | -3586542.3125 | 531.1098 | -50300239.5684 | -3586542.3125 | 664.3036 | -3586.5423 | 769.4871 | -3586.5423 | 3647.5451 | 0.18212
[6 empty] | 442869.057 | -3616770.124 | 530.1848 | -50304957.4719 | -3616770.124 | 442.8691 | -3616.7701 | 768.1642 | -3616.7701 | 3643.7836 | 0.12154
[6 empty] | 221434.5285 | -3634799.538 | 529.6323 | -50307787.8029 | -3634799.538 | 221.4345 | -3634.7995 | 767.3741 | -3634.7995 | 3641.5383 | 0.060808
[6 empty] | -5.2387e-10 | -3640791.7004 | 529.4485 | -50308731.1781 | -3640791.7004 | -5.2387e-13 | -3640.7917 | 767.1113 | -3640.7917 | 3640.7917 | -1.4389e-16
Note on B22: Autor: P_max no se da con reactiva 0 a la salida, por lo que el PF a la salida no es 1. La potencia es algo mayor que la rated porque la tension en bornas del stack de potencia es tb algo mayor
Note on B25: IF YES = '1' / NO = '0'

## V_1,04pu_DIG (hidden)
Inverter Voltage | 620 |  |  |  |  | P (W) | Q _Ii(VAr) | Vi_need | Q_Vdc (Var) | Q(Var) | P(kW) | Q_Ii(kVAr) | Vdc_min (V) | Q(kVAr) | S(kVA) | cos fi
Voltage operation pu | 1.04 |  |  | P_manual (kW), Q>0 | 3750 | 3750000 | 2306244.3153 | 699.1535 | 948432.4934 | 948432.4934 | 3750 | 2306.2443 | 1009.7894 | 948.4325 | 3868.0776 | 0.96947 | Capacitive
Line-Line Voltage (V) | 644.8 |  |  | P_manual (kW), Q<0 | 2846 | 2846000 | -2582664.1081 | 574.4826 | -51628112.8097 | -2582664.1081 | 2846 | -2582.6641 | 831.5102 | -2582.6641 | 3843.1588 | 0.74054 | Inductive
Nm: Number of modules | 3 |  |  |  |  | 0 | 4646345.8964 | 751.5444 | 1215122.178 | 1215122.178 | 0 | 4646.3459 | 1084.7085 | 1215.1222 | 1215.1222 | 0
f(Hz) | 50 | wg(Hz) | 314.1593 |  |  | 221434.5285 | 4640469.1319 | 751.4174 | 1214196.9453 | 1214196.9453 | 221.4345 | 4640.4691 | 1084.5269 | 1214.1969 | 1234.2234 | 0.17941
Height (m) | 2700 |  |  |  |  | 442869.057 | 4622788.9209 | 751.0352 | 1211421.0534 | 1211421.0534 | 442.8691 | 4622.7889 | 1083.9803 | 1211.4211 | 1289.8349 | 0.34335
Temperature Max (ºC) ( TM) | 33 | TM_H_corrected(ºC) | 44.25 |  |  | 664303.5855 | 4593153.3658 | 750.3941 | 1206793.9204 | 1206793.9204 | 664.3036 | 4593.1534 | 1083.0636 | 1206.7939 | 1377.5525 | 0.48223
Vdc_min (Tmax) | 951.5 | Vdc_min(sat) | 951.5 |  |  | 885738.114 | 4551301.9376 | 749.4879 | 1200314.5761 | 1200314.5761 | 885.7381 | 4551.3019 | 1081.7676 | 1200.3146 | 1491.7396 | 0.59376
TM_derating | 104.5% |  |  |  |  | 1107172.6425 | 4496853.6197 | 748.3072 | 1191981.6605 | 1191981.6605 | 1107.1726 | 4496.8536 | 1080.0793 | 1191.9817 | 1626.8533 | 0.68056
Vdc_min derating | 114.9% |  |  |  |  | 1328607.171 | 4429288.5345 | 746.8395 | 1181793.4227 | 1181793.4227 | 1328.6072 | 4429.2885 | 1077.9805 | 1181.7934 | 1778.1543 | 0.74718
Total derating@ TM | 120% |  |  |  |  | 1550041.6995 | 4347920.8557 | 745.0681 | 1169747.7191 | 1169747.7191 | 1550.0417 | 4347.9209 | 1075.4474 | 1169.7477 | 1941.8906 | 0.79821
Temperature Min (ºC) ( Tm) | -5 | Tm_H_corrected(ºC) | 6.25 |  |  | 1771476.228 | 4251859.4079 | 742.9714 | 1155842.0108 | 1155842.0108 | 1771.4762 | 4251.8594 | 1072.4492 | 1155.842 | 2115.2066 | 0.8375
Vdc_max (Tmin) | 1130 | Vdc_max(sat) | 1130 |  |  | 1992910.7564 | 4139950.0295 | 740.5214 | 1140073.3612 | 1140073.3612 | 1992.9108 | 4139.95 | 1068.9455 | 1140.0734 | 2295.9661 | 0.86801
Tm_derating | 111.6% |  |  |  |  | 2214345.2849 | 4010689.6523 | 737.6813 | 1122438.433 | 1122438.433 | 2214.3453 | 4010.6897 | 1064.8842 | 1122.4384 | 2482.5779 | 0.89195
Vdc_derating(V) | 106% |  |  |  |  | 2435779.8134 | 3862094.3598 | 734.4028 | 1102933.484 | 1102933.484 | 2435.7798 | 3862.0944 | 1060.196 | 1102.9335 | 2673.8522 | 0.91096
Total derating@ Tm | 118.3% |  |  |  |  | 2657214.3419 | 3691488.3761 | 730.6206 | 1081554.3639 | 1081554.3639 | 2657.2143 | 3691.4884 | 1054.7874 | 1081.5544 | 2868.8931 | 0.92622
[6 empty] | 2878648.8704 | 3495148.0623 | 726.2435 | 1058296.5095 | 1058296.5095 | 2878.6489 | 3495.1481 | 1048.5282 | 1058.2965 | 3067.0199 | 0.93858
Derating factor for TM | 118.3% |  |  |  |  | 3100083.3989 | 3267657.4034 | 721.1387 | 1033154.9395 | 1033154.9395 | 3100.0834 | 3267.6574 | 1041.2283 | 1033.1549 | 3267.7096 | 0.9487
[6 empty] | 3321517.9274 | 3000624.1614 | 715.1001 | 1006124.2495 | 1006124.2495 | 3321.5179 | 3000.6242 | 1032.5931 | 1006.1242 | 3470.5572 | 0.95706
Vi_max (V) | 658.3916 |  |  |  |  | 3542952.4559 | 2679748.7703 | 707.7757 | 977198.6058 | 977198.6058 | 3542.9525 | 2679.7488 | 1022.1193 | 977.1986 | 3675.2455 | 0.964
Ii (A) | 1242.32 |  |  |  |  | 3598311.088 | 2588339.7449 | 705.6753 | 969670.3834 | 969670.3834 | 3598.3111 | 2588.3397 | 1019.1157 | 969.6704 | 3726.6746 | 0.96556
P_max (W) (kW) | 4187125.6297 | P_base (kW) | 4187.1256 |  |  | 3653669.7202 | 2491284.1201 | 703.4383 | 962023.2345 | 962023.2345 | 3653.6697 | 2491.2841 | 1015.9167 | 962.0232 | 3778.1995 | 0.96704
Prated (W) | 4162367.1734 | Prated (kW) | 4162.3672 |  |  | 3709028.3523 | 2387724.0446 | 701.0434 | 954257.055 | 954257.055 | 3709.0284 | 2387.724 | 1012.4921 | 954.2571 | 3829.8169 | 0.96846
[6 empty] | 3764386.9844 | 2276540.258 | 698.4632 | 946371.7394 | 946371.7394 | 3764.387 | 2276.5403 | 1008.8023 | 946.3717 | 3881.524 | 0.96982
GPTech Inverter | 1 |  |  |  |  | 3819745.6165 | 2156223.9442 | 695.6602 | 938367.18 | 938367.18 | 3819.7456 | 2156.2239 | 1004.7941 | 938.3672 | 3933.3179 | 0.97113
Inverter output current (A) | 1250 |  |  |  |  | 3875104.2486 | 2024654.015 | 692.582 | 930243.2676 | 930243.2676 | 3875.1042 | 2024.654 | 1000.3923 | 930.2433 | 3985.1958 | 0.97237
[6 empty] | 3930462.8808 | 1878677.1277 | 689.1507 | 921999.8913 | 921999.8913 | 3930.4629 | 1878.6771 | 995.4856 | 921.9999 | 4037.1552 | 0.97357
Set Point Calculation Tool (@Tmax) | [5 empty] | 3985821.5129 | 1713222.109 | 685.2408 | 913636.9383 | 913636.9383 | 3985.8215 | 1713.2221 | 989.8944 | 913.6369 | 4089.1938 | 0.97472
P | 2846 | 2846 |  |  |  | 4041180.145 | 1519099.2602 | 680.6248 | 905154.294 | 905154.294 | 4041.1801 | 1519.0993 | 983.2935 | 905.1543 | 4141.3091 | 0.97582
| Q_ind_lim | -2582.6641 |  |  |  | 4096538.7771 | 1275809.5666 | 674.7951 | 896551.8421 | 896551.8421 | 4096.5388 | 1275.8096 | 974.957 | 896.5518 | 4193.4992 | 0.97688
| Q_cap_lim | 1061.844 |  |  |  | 4151897.4093 | 907624.9298 | 665.8756 | -51454098.2971 | 907624.9298 | 4151.8974 | 907.6249 | 962.202 | 907.6249 | 4249.9453 | 0.97693
Q | 0 | 0 |  |  |  | 4207256.0414 | 471617.8487 | 655.2871 | -51445255.8737 | 471617.8487 | 4207.256 | 471.6178 | 947.0606 | 471.6178 | 4233.6068 | 0.99378
PF | 1 | Io(P,Q) (A) | 2548.2923 |  |  | 4262614.6735 | 471617.8487 | 655.5127 | -51436293.2828 | 471617.8487 | 4262.6147 | 471.6178 | 947.3831 | 471.6178 | 4288.6253 | 0.99393
Vdc_min(V) | 923.601 |  |  |  |  | 4317973.3056 | 471617.8487 | 655.7411 | -51427210.4008 | 471617.8487 | 4317.9733 | 471.6178 | 947.7098 | 471.6178 | 4343.6525 | 0.99409
Vac_max(V) | 638.8818 |  |  |  |  | 4373331.9378 | 471617.8487 | 655.9724 | -51418007.1023 | 471617.8487 | 4373.3319 | 471.6178 | 948.0405 | 471.6178 | 4398.6879 | 0.99424
[6 empty] | 4428690.5699 | 471617.8487 | 656.2065 | -51408683.26 | 471617.8487 | 4428.6906 | 471.6178 | 948.3753 | 471.6178 | 4453.7314 | 0.99438
[6 empty] | 4373331.9378 | 471617.8487 | 655.9724 | -51418007.1023 | 471617.8487 | 4373.3319 | 471.6178 | 948.0405 | 471.6178 | 4398.6879 | 0.99424
[6 empty] | 4317973.3056 | 471617.8487 | 655.7411 | -51427210.4008 | 471617.8487 | 4317.9733 | 471.6178 | 947.7098 | 471.6178 | 4343.6525 | 0.99409
[6 empty] | 4262614.6735 | 471617.8487 | 655.5127 | -51436293.2828 | 471617.8487 | 4262.6147 | 471.6178 | 947.3831 | 471.6178 | 4288.6253 | 0.99393
[6 empty] | 4207256.0414 | 471617.8487 | 655.2871 | -51445255.8737 | 471617.8487 | 4207.256 | 471.6178 | 947.0606 | 471.6178 | 4233.6068 | 0.99378
[6 empty] | 4151897.4093 | 35610.7677 | 644.258 | -51454098.2971 | 35610.7677 | 4151.8974 | 35.6108 | 931.289 | 35.6108 | 4152.0501 | 0.99996
[6 empty] | 4096538.7771 | -332573.8692 | 634.9096 | -51462820.6749 | -332573.8692 | 4096.5388 | -332.5739 | 917.9208 | -332.5739 | 4110.0165 | 0.99672
[6 empty] | 4041180.145 | -575863.5627 | 628.6561 | -51471423.1268 | -575863.5627 | 4041.1801 | -575.8636 | 908.9783 | -575.8636 | 4082.0039 | 0.99
[6 empty] | 3985821.5129 | -769986.4115 | 623.6214 | -51479905.7711 | -769986.4115 | 3985.8215 | -769.9864 | 901.7786 | -769.9864 | 4059.5138 | 0.98185
[6 empty] | 3930462.8808 | -935441.4303 | 619.2979 | -51488268.7241 | -935441.4303 | 3930.4629 | -935.4414 | 895.596 | -935.4414 | 4040.2462 | 0.97283
[6 empty] | 3875104.2486 | -1081418.3176 | 615.4582 | -51496512.1004 | -1081418.3176 | 3875.1042 | -1081.4183 | 890.1052 | -1081.4183 | 4023.1702 | 0.9632
[6 empty] | 3819745.6165 | -1212988.2467 | 611.9768 | -51504636.0128 | -1212988.2467 | 3819.7456 | -1212.9882 | 885.1268 | -1212.9882 | 4007.7172 | 0.9531
[6 empty] | 3764386.9844 | -1333304.5605 | 608.7757 | -51512640.5722 | -1333304.5605 | 3764.387 | -1333.3046 | 880.5492 | -1333.3046 | 3993.5336 | 0.94262
[6 empty] | 3709028.3523 | -1444488.3471 | 605.8026 | -51520525.8878 | -1444488.3471 | 3709.0284 | -1444.4883 | 876.2977 | -1444.4883 | 3980.3816 | 0.93183
[6 empty] | 3653669.7202 | -1548048.4227 | 603.0201 | -51528292.0673 | -1548048.4227 | 3653.6697 | -1548.0484 | 872.3187 | -1548.0484 | 3968.0923 | 0.92076
[6 empty] | 3598311.088 | -1645104.0474 | 600.4007 | -51535939.2162 | -1645104.0474 | 3598.3111 | -1645.104 | 868.573 | -1645.104 | 3956.5402 | 0.90946
[6 empty] | 3542952.4559 | -1736513.0729 | 597.9232 | -51543467.4386 | -1736513.0729 | 3542.9525 | -1736.5131 | 865.0302 | -1736.5131 | 3945.6292 | 0.89794
[6 empty] | 3321517.9274 | -2057388.464 | 589.1439 | -51572393.0823 | -2057388.464 | 3321.5179 | -2057.3885 | 852.4758 | -2057.3885 | 3907.087 | 0.85013
[6 empty] | 3100083.3989 | -2324421.706 | 581.7368 | -51599423.7723 | -2324421.706 | 3100.0834 | -2324.4217 | 841.8836 | -2324.4217 | 3874.7198 | 0.80008
[6 empty] | 2878648.8704 | -2551912.3649 | 575.3513 | -51624565.3423 | -2551912.3649 | 2878.6489 | -2551.9124 | 832.7523 | -2551.9124 | 3846.9307 | 0.7483
[6 empty] | 2657214.3419 | -2748252.6786 | 569.7826 | -51647823.1968 | -2748252.6786 | 2657.2143 | -2748.2527 | 824.7891 | -2748.2527 | 3822.7844 | 0.6951
[6 empty] | 2435779.8134 | -2918858.6624 | 564.8992 | -51669202.3168 | -2918858.6624 | 2435.7798 | -2918.8587 | 817.8059 | -2918.8587 | 3801.6785 | 0.64071
[6 empty] | 2214345.2849 | -3067453.9548 | 560.6112 | -51688707.2658 | -3067453.9548 | 2214.3453 | -3067.454 | 811.6741 | -3067.454 | 3783.1995 | 0.58531
[6 empty] | 1992910.7564 | -3196714.3321 | 556.8543 | -51706342.194 | -3196714.3321 | 1992.9108 | -3196.7143 | 806.3017 | -3196.7143 | 3767.0513 | 0.52904
[6 empty] | 1771476.228 | -3308623.7104 | 553.5812 | -51722110.8436 | -3308623.7104 | 1771.4762 | -3308.6237 | 801.621 | -3308.6237 | 3753.0146 | 0.47201
[6 empty] | 1550041.6995 | -3404685.1582 | 550.756 | -51736016.5519 | -3404685.1582 | 1550.0417 | -3404.6852 | 797.581 | -3404.6852 | 3740.9237 | 0.41435
[6 empty] | 1328607.171 | -3486052.837 | 548.3516 | -51748062.2555 | -3486052.837 | 1328.6072 | -3486.0528 | 794.1427 | -3486.0528 | 3730.6516 | 0.35613
[6 empty] | 1107172.6425 | -3553617.9222 | 546.347 | -51758250.4933 | -3553617.9222 | 1107.1726 | -3553.6179 | 791.2762 | -3553.6179 | 3722.1004 | 0.29746
[6 empty] | 885738.114 | -3608066.2402 | 544.7262 | -51766583.4089 | -3608066.2402 | 885.7381 | -3608.0662 | 788.9584 | -3608.0662 | 3715.195 | 0.23841
[6 empty] | 664303.5855 | -3649917.6683 | 543.4771 | -51773062.7532 | -3649917.6683 | 664.3036 | -3649.9177 | 787.1722 | -3649.9177 | 3709.8785 | 0.17906
[6 empty] | 442869.057 | -3679553.2234 | 542.5908 | -51777689.8862 | -3679553.2234 | 442.8691 | -3679.5532 | 785.9049 | -3679.5532 | 3706.1091 | 0.1195
[6 empty] | 221434.5285 | -3697233.4345 | 542.0614 | -51780465.7781 | -3697233.4345 | 221.4345 | -3697.2334 | 785.1478 | -3697.2334 | 3703.8586 | 0.059785
[6 empty] | -5.2387e-10 | -3703110.1989 | 541.8853 | -51781391.0108 | -3703110.1989 | -5.2387e-13 | -3703.1102 | 784.896 | -3703.1102 | 3703.1102 | -1.4147e-16
Note on B22: Autor: P_max no se da con reactiva 0 a la salida, por lo que el PF a la salida no es 1. La potencia es algo mayor que la rated porque la tension en bornas del stack de potencia es tb algo mayor
Note on B25: IF YES = '1' / NO = '0'

## V_1,06pu_DIG (hidden)
Inverter Voltage | 620 |  |  |  |  | P (W) | Q _Ii(VAr) | Vi_need | Q_Vdc (Var) | Q(Var) | P(kW) | Q_Ii(kVAr) | Vdc_min (V) | Q(kVAr) | S(kVA) | cos fi
Voltage operation pu | 1.06 |  |  | P_manual (kW), Q>0 | 3750 | 3750000 | 2500558.4251 | 714.6836 | 481317.4136 | 481317.4136 | 3750 | 2500.5584 | 1031.9976 | 481.3174 | 3780.7627 | 0.99186 | Capacitive
Line-Line Voltage (V) | 657.2 |  |  | P_manual (kW), Q<0 | 2846 | 2846000 | -2673200.7366 | 585.4364 | -53122381.5767 | -2673200.7366 | 2846 | -2673.2007 | 847.1741 | -2673.2007 | 3904.5766 | 0.72889 | Inductive
Nm: Number of modules | 3 |  |  |  |  | 0 | 4744942.691 | 763.9812 | 742925.5172 | 742925.5172 | 0 | 4744.9427 | 1102.4931 | 742.9255 | 742.9255 | 0
f(Hz) | 50 | wg(Hz) | 314.1593 |  |  | 221434.5285 | 4739176.9608 | 763.8586 | 742017.7423 | 742017.7423 | 221.4345 | 4739.177 | 1102.3178 | 742.0177 | 774.3537 | 0.28596
Height (m) | 2700 |  |  |  |  | 442869.057 | 4721832.6375 | 763.4898 | 739294.2346 | 739294.2346 | 442.8691 | 4721.8326 | 1101.7904 | 739.2942 | 861.794 | 0.51389
Temperature Max (ºC) ( TM) | 33 | TM_H_corrected(ºC) | 44.25 |  |  | 664303.5855 | 4692766.3755 | 762.8713 | 734754.4446 | 734754.4446 | 664.3036 | 4692.7664 | 1100.906 | 734.7544 | 990.5369 | 0.67065
Vdc_min (Tmax) | 951.5 | Vdc_min(sat) | 951.5 |  |  | 885738.114 | 4651732.5819 | 761.9973 | 728397.4558 | 728397.4558 | 885.7381 | 4651.7326 | 1099.6562 | 728.3975 | 1146.7759 | 0.77237
TM_derating | 104.5% |  |  |  |  | 1107172.6425 | 4598372.6887 | 760.8593 | 720221.9841 | 720221.9841 | 1107.1726 | 4598.3727 | 1098.0288 | 720.222 | 1320.8145 | 0.83825
Vdc_min derating | 114.9% |  |  |  |  | 1328607.171 | 4532198.5939 | 759.4456 | 710226.376 | 710226.376 | 1328.6072 | 4532.1986 | 1096.0072 | 710.2264 | 1506.5253 | 0.8819
Total derating@ TM | 120% |  |  |  |  | 1550041.6995 | 4452568.3767 | 757.7409 | 698408.6073 | 698408.6073 | 1550.0417 | 4452.5684 | 1093.5696 | 698.4086 | 1700.1188 | 0.91173
Temperature Min (ºC) ( Tm) | -5 | Tm_H_corrected(ºC) | 6.25 |  |  | 1771476.228 | 4358651.2207 | 755.7255 | 684766.2808 | 684766.2808 | 1771.4762 | 4358.6512 | 1090.6875 | 684.7663 | 1899.219 | 0.93274
Vdc_max (Tmin) | 1130 | Vdc_max(sat) | 1130 |  |  | 1992910.7564 | 4249376.5441 | 753.3737 | 669296.6242 | 669296.6242 | 1992.9108 | 4249.3765 | 1087.3244 | 669.2966 | 2102.2967 | 0.94797
Tm_derating | 111.6% |  |  |  |  | 2214345.2849 | 4123358.9871 | 750.6524 | 651996.4868 | 651996.4868 | 2214.3453 | 4123.359 | 1083.433 | 651.9965 | 2308.338 | 0.95928
Vdc_derating(V) | 106% |  |  |  |  | 2435779.8134 | 3978784.7602 | 747.5182 | 632862.3366 | 632862.3366 | 2435.7798 | 3978.7848 | 1078.951 | 632.8623 | 2516.6521 | 0.96787
Total derating@ Tm | 118.3% |  |  |  |  | 2657214.3419 | 3813232.9219 | 743.913 | 611890.2566 | 611890.2566 | 2657.2143 | 3813.2329 | 1073.7956 | 611.8903 | 2726.7559 | 0.9745
[6 empty] | 2878648.8704 | 3623380.2572 | 739.757 | 589075.9408 | 589075.9408 | 2878.6489 | 3623.3803 | 1067.8525 | 589.0759 | 2938.3039 | 0.9797
Derating factor for TM | 118.3% |  |  |  |  | 3100083.3989 | 3404481.7898 | 734.936 | 564414.6895 | 564414.6895 | 3100.0834 | 3404.4818 | 1060.9584 | 564.4147 | 3151.0444 | 0.98383
[6 empty] | 3321517.9274 | 3149374.8957 | 729.2773 | 537901.4045 | 537901.4045 | 3321.5179 | 3149.3749 | 1052.8665 | 537.9014 | 3364.7911 | 0.98714
Vi_max (V) | 658.3916 |  |  |  |  | 3542952.4559 | 2846328.8489 | 722.4976 | 509530.5841 | 509530.5841 | 3542.9525 | 2846.3288 | 1043.1716 | 509.5306 | 3579.4041 | 0.98982
Ii (A) | 1242.32 |  |  |  |  | 3598311.088 | 2760895.5904 | 720.5748 | 502146.9554 | 502146.9554 | 3598.3111 | 2760.8956 | 1040.422 | 502.147 | 3633.1796 | 0.9904
P_max (W) (kW) | 4267647.2764 | P_base (kW) | 4267.6473 |  |  | 3653669.7202 | 2670715.3448 | 718.5396 | 494646.7668 | 494646.7668 | 3653.6697 | 2670.7153 | 1037.5116 | 494.6468 | 3687.0012 | 0.99096
Prated (W) | 4242412.6959 | Prated (kW) | 4242.4127 |  |  | 3709028.3523 | 2575172.3256 | 716.377 | 487029.9205 | 487029.9205 | 3709.0284 | 2575.1723 | 1034.4191 | 487.0299 | 3740.8675 | 0.99149
[6 empty] | 3764386.9844 | 2473491.7508 | 714.0683 | 479296.3166 | 479296.3166 | 3764.387 | 2473.4918 | 1031.1177 | 479.2963 | 3794.7772 | 0.99199
GPTech Inverter | 1 |  |  |  |  | 3819745.6165 | 2364675.2374 | 711.5893 | 471445.8538 | 471445.8538 | 3819.7456 | 2364.6752 | 1027.5727 | 471.4459 | 3848.7294 | 0.99247
Inverter output current (A) | 1250 |  |  |  |  | 3875104.2486 | 2247397.7838 | 708.9078 | 463478.4293 | 463478.4293 | 3875.1042 | 2247.3978 | 1023.7382 | 463.4784 | 3902.7228 | 0.99292
[6 empty] | 3930462.8808 | 2119834.0253 | 705.9796 | 455393.9383 | 455393.9383 | 3930.4629 | 2119.834 | 1019.5509 | 455.3939 | 3956.7565 | 0.99335
Set Point Calculation Tool (@Tmax) | [5 empty] | 3985821.5129 | 1979343.3273 | 702.7405 | 447192.2746 | 447192.2746 | 3985.8215 | 1979.3433 | 1014.919 | 447.1923 | 4010.8296 | 0.99376
P | 2846 | 2846 |  |  |  | 4041180.145 | 1821841.327 | 699.0914 | 438873.3302 | 438873.3302 | 4041.1801 | 1821.8413 | 1009.7007 | 438.8733 | 4064.9412 | 0.99415
| Q_ind_lim | -2673.2007 |  |  |  | 4096538.7771 | 1640362.2156 | 694.863 | 430436.9954 | 430436.9954 | 4096.5388 | 1640.3622 | 1003.6541 | 430.437 | 4119.0904 | 0.99453
| Q_cap_lim | 592.5557 |  |  |  | 4151897.4093 | 1420989.353 | 689.7171 | 421883.159 | 421883.159 | 4151.8974 | 1420.9894 | 996.2955 | 421.8832 | 4173.2766 | 0.99488
Q | 0 | 0 |  |  |  | 4207256.0414 | 1125633.8494 | 682.7276 | 413211.7079 | 413211.7079 | 4207.256 | 1125.6338 | 986.3004 | 413.2117 | 4227.4989 | 0.99521
PF | 1 | Io(P,Q) (A) | 2500.2113 |  |  | 4262614.6735 | 489931.4116 | 667.465 | 404422.5274 | 404422.5274 | 4262.6147 | 489.9314 | 964.4749 | 404.4225 | 4281.7568 | 0.99553
Vdc_min(V) | 940.7428 |  |  |  |  | 4317973.3056 | 489931.4116 | 667.6809 | 395515.501 | 395515.501 | 4317.9733 | 489.9314 | 964.7837 | 395.5155 | 4336.0496 | 0.99583
Vac_max(V) | 650.8691 |  |  |  |  | 4373331.9378 | 489931.4116 | 667.8996 | 386490.5107 | 386490.5107 | 4373.3319 | 489.9314 | 965.0964 | 386.4905 | 4390.3767 | 0.99612
[6 empty] | 4428690.5699 | 489931.4116 | 668.1209 | 377347.4364 | 377347.4364 | 4428.6906 | 489.9314 | 965.4129 | 377.3474 | 4444.7375 | 0.99639
[6 empty] | 4373331.9378 | 489931.4116 | 667.8996 | -52916316.3802 | 489931.4116 | 4373.3319 | 489.9314 | 965.0964 | 489.9314 | 4400.6892 | 0.99378
[6 empty] | 4317973.3056 | 489931.4116 | 667.6809 | -52925341.3706 | 489931.4116 | 4317.9733 | 489.9314 | 964.7837 | 489.9314 | 4345.679 | 0.99362
[6 empty] | 4262614.6735 | 489931.4116 | 667.465 | -52934248.397 | 489931.4116 | 4262.6147 | 489.9314 | 964.4749 | 489.9314 | 4290.6779 | 0.99346
[6 empty] | 4207256.0414 | -145771.0262 | 651.7848 | -52943037.5775 | -145771.0262 | 4207.256 | -145.771 | 942.0522 | -145.771 | 4209.7806 | 0.9994
[6 empty] | 4151897.4093 | -441126.5297 | 644.3839 | -52951709.0286 | -441126.5297 | 4151.8974 | -441.1265 | 931.469 | -441.1265 | 4175.2658 | 0.9944
[6 empty] | 4096538.7771 | -660499.3923 | 638.8315 | -52960262.865 | -660499.3923 | 4096.5388 | -660.4994 | 923.529 | -660.4994 | 4149.4445 | 0.98725
[6 empty] | 4041180.145 | -841978.5038 | 634.2015 | -52968699.1998 | -841978.5038 | 4041.1801 | -841.9785 | 916.9081 | -841.9785 | 4127.9613 | 0.97898
[6 empty] | 3985821.5129 | -999480.504 | 630.1556 | -52977018.1442 | -999480.504 | 3985.8215 | -999.4805 | 911.1225 | -999.4805 | 4109.2255 | 0.96997
[6 empty] | 3930462.8808 | -1139971.202 | 626.5246 | -52985219.8079 | -1139971.202 | 3930.4629 | -1139.9712 | 905.9302 | -1139.9712 | 4092.4409 | 0.96042
[6 empty] | 3875104.2486 | -1267534.9605 | 623.2094 | -52993304.2989 | -1267534.9605 | 3875.1042 | -1267.535 | 901.1895 | -1267.535 | 4077.1409 | 0.95045
[6 empty] | 3819745.6165 | -1384812.4141 | 620.1459 | -53001271.7234 | -1384812.4141 | 3819.7456 | -1384.8124 | 896.8087 | -1384.8124 | 4063.0238 | 0.94012
[6 empty] | 3764386.9844 | -1493628.9275 | 617.2898 | -53009122.1862 | -1493628.9275 | 3764.387 | -1493.6289 | 892.7245 | -1493.6289 | 4049.8811 | 0.92951
[6 empty] | 3709028.3523 | -1595309.5023 | 614.6091 | -53016855.7901 | -1595309.5023 | 3709.0284 | -1595.3095 | 888.891 | -1595.3095 | 4037.5616 | 0.91863
[6 empty] | 3653669.7202 | -1690852.5215 | 612.0794 | -53024472.6364 | -1690852.5215 | 3653.6697 | -1690.8525 | 885.2735 | -1690.8525 | 4025.9514 | 0.90753
[6 empty] | 3598311.088 | -1781032.7671 | 609.6821 | -53031972.825 | -1781032.7671 | 3598.3111 | -1781.0328 | 881.8454 | -1781.0328 | 4014.9621 | 0.89623
[6 empty] | 3542952.4559 | -1866466.0256 | 607.4022 | -53039356.4537 | -1866466.0256 | 3542.9525 | -1866.466 | 878.5852 | -1866.466 | 4004.5234 | 0.88474
[6 empty] | 3321517.9274 | -2169512.0725 | 599.2453 | -53067727.2741 | -2169512.0725 | 3321.5179 | -2169.5121 | 866.9208 | -2169.5121 | 3967.2741 | 0.83723
[6 empty] | 3100083.3989 | -2424618.9665 | 592.2917 | -53094240.559 | -2424618.9665 | 3100.0834 | -2424.619 | 856.9771 | -2424.619 | 3935.6441 | 0.78769
[6 empty] | 2878648.8704 | -2643517.434 | 586.2592 | -53118901.8104 | -2643517.434 | 2878.6489 | -2643.5174 | 848.3507 | -2643.5174 | 3908.2993 | 0.73655
[6 empty] | 2657214.3419 | -2833370.0986 | 580.9765 | -53141716.1262 | -2833370.0986 | 2657.2143 | -2833.3701 | 840.7964 | -2833.3701 | 3884.4271 | 0.68407
[6 empty] | 2435779.8134 | -2998921.9369 | 576.3305 | -53162688.2062 | -2998921.9369 | 2435.7798 | -2998.9219 | 834.1526 | -2998.9219 | 3863.4901 | 0.63046
[6 empty] | 2214345.2849 | -3143496.1638 | 572.2423 | -53181822.3564 | -3143496.1638 | 2214.3453 | -3143.4962 | 828.3065 | -3143.4962 | 3845.1129 | 0.57589
[6 empty] | 1992910.7564 | -3269513.7208 | 568.6549 | -53199122.4938 | -3269513.7208 | 1992.9108 | -3269.5137 | 823.1765 | -3269.5137 | 3829.0225 | 0.52048
[6 empty] | 1771476.228 | -3378788.3974 | 565.5257 | -53214592.1504 | -3378788.3974 | 1771.4762 | -3378.7884 | 818.7017 | -3378.7884 | 3815.0149 | 0.46434
[6 empty] | 1550041.6995 | -3472705.5535 | 562.8223 | -53228234.4768 | -3472705.5535 | 1550.0417 | -3472.7056 | 814.8359 | -3472.7056 | 3802.9348 | 0.40759
[6 empty] | 1328607.171 | -3552335.7706 | 560.52 | -53240052.2456 | -3552335.7706 | 1328.6072 | -3552.3358 | 811.5436 | -3552.3358 | 3792.6622 | 0.35031
[6 empty] | 1107172.6425 | -3618509.8654 | 558.5995 | -53250047.8537 | -3618509.8654 | 1107.1726 | -3618.5099 | 808.7973 | -3618.5099 | 3784.1042 | 0.29259
[6 empty] | 885738.114 | -3671869.7586 | 557.0461 | -53258223.3254 | -3671869.7586 | 885.7381 | -3671.8698 | 806.5759 | -3671.8698 | 3777.1894 | 0.2345
[6 empty] | 664303.5855 | -3712903.5522 | 555.8486 | -53264580.3141 | -3712903.5522 | 664.3036 | -3712.9036 | 804.8635 | -3712.9036 | 3771.8632 | 0.17612
[6 empty] | 442869.057 | -3741969.8142 | 554.9988 | -53269120.1042 | -3741969.8142 | 442.8691 | -3741.9698 | 803.6482 | -3741.9698 | 3768.0859 | 0.11753
[6 empty] | 221434.5285 | -3759314.1375 | 554.491 | -53271843.6119 | -3759314.1375 | 221.4345 | -3759.3141 | 802.9222 | -3759.3141 | 3765.8301 | 0.058801
[6 empty] | -5.2387e-10 | -3765079.8677 | 554.3221 | -53272751.3868 | -3765079.8677 | -5.2387e-13 | -3765.0799 | 802.6807 | -3765.0799 | 3765.0799 | -1.3914e-16
Note on B22: Autor: P_max no se da con reactiva 0 a la salida, por lo que el PF a la salida no es 1. La potencia es algo mayor que la rated porque la tension en bornas del stack de potencia es tb algo mayor
Note on B25: IF YES = '1' / NO = '0'

## V_1,08pu_DIG (hidden)
Inverter Voltage | 620 |  |  |  |  | P (W) | Q _Ii(VAr) | Vi_need | Q_Vdc (Var) | Q(Var) | P(kW) | Q_Ii(kVAr) | Vdc_min (V) | Q(kVAr) | S(kVA) | cos fi
Voltage operation pu | 1.08 |  |  | P_manual (kW), Q>0 | 3750 | 3750000 | 2683973.8854 | 729.845 | -4689.135 | -4689.135 | 3750 | 2683.9739 | 1053.6784 | -4.6891 | 3750.0029 | 1 | Capacitive
Line-Line Voltage (V) | 669.6 |  |  | P_manual (kW), Q<0 | 2846 | 2846000 | -2761736.836 | 596.4934 | -54635242.279 | -2761736.836 | 2846 | -2761.7368 | 862.9855 | -2761.7368 | 3965.7164 | 0.71765 | Inductive
Nm: Number of modules | 3 |  |  |  |  | 0 | 4843888.3153 | 776.418 | 252028.3132 | 252028.3132 | 0 | 4843.8883 | 1120.2778 | 252.0283 | 252.0283 | 0
f(Hz) | 50 | wg(Hz) | 314.1593 |  |  | 221434.5285 | 4838229.4988 | 776.2997 | 251137.3495 | 251137.3495 | 221.4345 | 4838.2295 | 1120.1085 | 251.1373 | 334.8182 | 0.66136
Height (m) | 2700 |  |  |  |  | 442869.057 | 4821208.4979 | 775.9435 | 248464.2854 | 248464.2854 | 442.8691 | 4821.2085 | 1119.5992 | 248.4643 | 507.8066 | 0.87212
Temperature Max (ºC) ( TM) | 33 | TM_H_corrected(ºC) | 44.25 |  |  | 664303.5855 | 4792689.8868 | 775.3464 | 244008.6012 | 244008.6012 | 664.3036 | 4792.6899 | 1118.7454 | 244.0086 | 707.7001 | 0.93868
Vdc_min (Tmax) | 951.5 | Vdc_min(sat) | 957.528 |  |  | 885738.114 | 4752441.8801 | 774.503 | 237769.4308 | 237769.4308 | 885.7381 | 4752.4419 | 1117.5393 | 237.7694 | 917.0967 | 0.96581
TM_derating | 104.5% |  |  |  |  | 1107172.6425 | 4700126.6071 | 773.4053 | 229745.5598 | 229745.5598 | 1107.1726 | 4700.1266 | 1115.9696 | 229.7456 | 1130.7583 | 0.97914
Vdc_min derating | 114.6% |  |  |  |  | 1328607.171 | 4635285.1524 | 772.0426 | 219935.4253 | 219935.4253 | 1328.6072 | 4635.2852 | 1114.0209 | 219.9354 | 1346.688 | 0.98657
Total derating@ TM | 119.7% |  |  |  |  | 1550041.6995 | 4557315.7295 | 770.4008 | 208337.1139 | 208337.1139 | 1550.0417 | 4557.3157 | 1111.6732 | 208.3371 | 1563.9801 | 0.99109
Temperature Min (ºC) ( Tm) | -5 | Tm_H_corrected(ºC) | 6.25 |  |  | 1771476.228 | 4465442.3573 | 768.4618 | 194948.3596 | 194948.3596 | 1771.4762 | 4465.4424 | 1108.9004 | 194.9484 | 1782.1708 | 0.994
Vdc_max (Tmin) | 1130 | Vdc_max(sat) | 1130 |  |  | 1992910.7564 | 4358669.8054 | 766.2021 | 179766.5423 | 179766.5423 | 1992.9108 | 4358.6698 | 1105.669 | 179.7665 | 2001.0021 | 0.99596
Tm_derating | 111.6% |  |  |  |  | 2214345.2849 | 4235717.8238 | 763.5918 | 162788.6843 | 162788.6843 | 2214.3453 | 4235.7178 | 1101.9362 | 162.7887 | 2220.321 | 0.99731
Vdc_derating(V) | 106% |  |  |  |  | 2435779.8134 | 4094922.7348 | 760.5916 | 144011.4483 | 144011.4483 | 2435.7798 | 4094.9227 | 1097.6459 | 144.0114 | 2440.0333 | 0.99826
Total derating@ Tm | 118.3% |  |  |  |  | 2657214.3419 | 3934085.0739 | 757.1498 | 123431.1334 | 123431.1334 | 2657.2143 | 3934.0851 | 1092.7241 | 123.4311 | 2660.0796 | 0.99892
[6 empty] | 2878648.8704 | 3750222.8975 | 753.196 | 101043.6717 | 101043.6717 | 2878.6489 | 3750.2229 | 1087.0702 | 101.0437 | 2880.4217 | 0.99938
Derating factor for TM | 118.3% |  |  |  |  | 3100083.3989 | 3539148.4428 | 748.6312 | 76844.6242 | 76844.6242 | 3100.0834 | 3539.1484 | 1080.5427 | 76.8446 | 3101.0357 | 0.99969
[6 empty] | 3321517.9274 | 3294683.7446 | 743.3094 | 50829.1763 | 50829.1763 | 3321.5179 | 3294.6837 | 1072.9324 | 50.8292 | 3321.9068 | 0.99988
Vi_max (V) | 662.607 |  |  |  |  | 3542952.4559 | 3007046.604 | 736.9985 | 22992.1329 | 22992.1329 | 3542.9525 | 3007.0466 | 1063.9078 | 22.9921 | 3543.0271 | 0.99998
Ii (A) | 1242.32 |  |  |  |  | 3598311.088 | 2926637.6027 | 735.2246 | 15747.6024 | 15747.6024 | 3598.3111 | 2926.6376 | 1061.3712 | 15.7476 | 3598.3455 | 0.99999
P_max (W) (kW) | 4348168.9232 | P_base (kW) | 4348.1689 |  |  | 3653669.7202 | 2842148.1905 | 733.356 | 8388.7843 | 8388.7843 | 3653.6697 | 2842.1482 | 1058.6991 | 8.3888 | 3653.6794 | 1
Prated (W) | 4322458.2185 | Prated (kW) | 4322.4582 |  |  | 3709028.3523 | 2753117.6245 | 731.3819 | 915.586 | 915.586 | 3709.0284 | 2753.1176 | 1055.8761 | 0.91559 | 3709.0285 | 1
[6 empty] | 3764386.9844 | 2658981.9388 | 729.2888 | -6672.0865 | -6672.0865 | 3764.387 | 2658.9819 | 1052.8829 | -6.6721 | 3764.3929 | 1
GPTech Inverter | 1 |  |  |  |  | 3819745.6165 | 2559038.1275 | 727.0599 | -14374.3288 | -14374.3288 | 3819.7456 | 2559.0381 | 1049.6956 | -14.3743 | 3819.7727 | 0.99999
Inverter output current (A) | 1250 |  |  |  |  | 3875104.2486 | 2452390.4911 | 724.6739 | -22191.2381 | -22191.2381 | 3875.1042 | 2452.3905 | 1046.2837 | -22.1912 | 3875.1678 | 0.99998
[6 empty] | 3930462.8808 | 2337866.895 | 722.103 | -30122.9131 | -30122.9131 | 3930.4629 | 2337.8669 | 1042.6072 | -30.1229 | 3930.5783 | 0.99997
Set Point Calculation Tool (@Tmax) | [5 empty] | 3985821.5129 | 2213881.277 | 719.3093 | -38169.4542 | -38169.4542 | 3985.8215 | 2213.8813 | 1038.6122 | -38.1695 | 3986.0043 | 0.99995
P | 2846 | 2846 |  |  |  | 4041180.145 | 2078192.9674 | 716.2394 | -46330.9632 | -46330.9632 | 4041.1801 | 2078.193 | 1034.2223 | -46.331 | 4041.4457 | 0.99993
| Q_ind_lim | -2761.7368 |  |  |  | 4096538.7771 | 1927448.4638 | 712.8133 | -54607.5435 | -54607.5435 | 4096.5388 | 1927.4485 | 1029.3231 | -54.6075 | 4096.9027 | 0.99991
| Q_cap_lim | 104.4583 |  |  |  | 4151897.4093 | 1756202.0762 | 708.9013 | -62999.3002 | -62999.3002 | 4151.8974 | 1756.2021 | 1023.7288 | -62.9993 | 4152.3753 | 0.99988
Q | 0 | 0 |  |  |  | 4207256.0414 | 1554430.8372 | 704.264 | -71506.3399 | -71506.3399 | 4207.256 | 1554.4308 | 1017.0975 | -71.5063 | 4207.8637 | 0.99986
PF | 1 | Io(P,Q) (A) | 2453.9111 |  |  | 4262614.6735 | 1299096.5826 | 698.3515 | -80128.7709 | -80128.7709 | 4262.6147 | 1299.0966 | 1008.6426 | -80.1288 | 4263.3677 | 0.99982
Vdc_min(V) | 957.9075 |  |  |  |  | 4317973.3056 | 895743.6836 | 688.9082 | -88866.7029 | -88866.7029 | 4317.9733 | 895.7437 | 995.1387 | -88.8667 | 4318.8877 | 0.99979
Vac_max(V) | 662.8724 |  |  |  |  | 4373331.9378 | 508593.8043 | 679.8632 | -97720.2475 | -97720.2475 | 4373.3319 | 508.5938 | 982.2044 | -97.7202 | 4374.4236 | 0.99975
[6 empty] | 4428690.5699 | 508593.8043 | 680.0727 | -106689.5176 | -106689.5176 | 4428.6906 | 508.5938 | 982.504 | -106.6895 | 4429.9755 | 0.99971
[6 empty] | 4373331.9378 | 508593.8043 | 679.8632 | -54433063.7453 | 508593.8043 | 4373.3319 | 508.5938 | 982.2044 | 508.5938 | 4402.8059 | 0.99331
[6 empty] | 4317973.3056 | 121443.925 | 670.4075 | -54441917.2899 | 121443.925 | 4317.9733 | 121.4439 | 968.6827 | 121.4439 | 4319.6808 | 0.9996
[6 empty] | 4262614.6735 | -281908.9739 | 660.5648 | -54450655.2219 | -281908.9739 | 4262.6147 | -281.909 | 954.6077 | -281.909 | 4271.9266 | 0.99782
[6 empty] | 4207256.0414 | -537243.2286 | 654.2575 | -54459277.6529 | -537243.2286 | 4207.256 | -537.2432 | 945.5883 | -537.2432 | 4241.4188 | 0.99195
[6 empty] | 4151897.4093 | -739014.4676 | 649.2301 | -54467784.6926 | -739014.4676 | 4151.8974 | -739.0145 | 938.399 | -739.0145 | 4217.1548 | 0.98453
[6 empty] | 4096538.7771 | -910260.8551 | 644.9324 | -54476176.4493 | -910260.8551 | 4096.5388 | -910.2609 | 932.2534 | -910.2609 | 4196.4515 | 0.97619
[6 empty] | 4041180.145 | -1061005.3588 | 641.1254 | -54484453.0296 | -1061005.3588 | 4041.1801 | -1061.0054 | 926.8094 | -1061.0054 | 4178.1419 | 0.96722
[6 empty] | 3985821.5129 | -1196693.6684 | 637.6793 | -54492614.5386 | -1196693.6684 | 3985.8215 | -1196.6937 | 921.8814 | -1196.6937 | 4161.5921 | 0.95776
[6 empty] | 3930462.8808 | -1320679.2863 | 634.514 | -54500661.0796 | -1320679.2863 | 3930.4629 | -1320.6793 | 917.355 | -1320.6793 | 4146.412 | 0.94792
[6 empty] | 3875104.2486 | -1435202.8824 | 631.5761 | -54508592.7547 | -1435202.8824 | 3875.1042 | -1435.2029 | 913.1539 | -1435.2029 | 4132.3408 | 0.93775
[6 empty] | 3819745.6165 | -1541850.5188 | 628.828 | -54516409.664 | -1541850.5188 | 3819.7456 | -1541.8505 | 909.224 | -1541.8505 | 4119.194 | 0.9273
[6 empty] | 3764386.9844 | -1641794.3302 | 626.2416 | -54524111.9063 | -1641794.3302 | 3764.387 | -1641.7943 | 905.5255 | -1641.7943 | 4106.8355 | 0.91661
[6 empty] | 3709028.3523 | -1735930.0158 | 623.7958 | -54531699.5788 | -1735930.0158 | 3709.0284 | -1735.93 | 902.028 | -1735.93 | 4095.1611 | 0.90571
[6 empty] | 3653669.7202 | -1824960.5819 | 621.4737 | -54539172.777 | -1824960.5819 | 3653.6697 | -1824.9606 | 898.7074 | -1824.9606 | 4084.0891 | 0.89461
[6 empty] | 3598311.088 | -1909449.9941 | 619.262 | -54546531.5952 | -1909449.9941 | 3598.3111 | -1909.45 | 895.5447 | -1909.45 | 4073.554 | 0.88333
[6 empty] | 3542952.4559 | -1989858.9954 | 617.1498 | -54553776.1257 | -1989858.9954 | 3542.9525 | -1989.859 | 892.5242 | -1989.859 | 4063.5023 | 0.8719
[6 empty] | 3321517.9274 | -2277496.1359 | 609.5341 | -54581613.169 | -2277496.1359 | 3321.5179 | -2277.4961 | 881.6338 | -2277.4961 | 4027.3403 | 0.82474
[6 empty] | 3100083.3989 | -2521960.8342 | 602.9859 | -54607628.6169 | -2521960.8342 | 3100.0834 | -2521.9608 | 872.2698 | -2521.9608 | 3996.3488 | 0.77573
[6 empty] | 2878648.8704 | -2733035.2889 | 597.2742 | -54631827.6645 | -2733035.2889 | 2878.6489 | -2733.0353 | 864.1022 | -2733.0353 | 3969.3956 | 0.72521
[6 empty] | 2657214.3419 | -2916897.4653 | 592.2541 | -54654215.1262 | -2916897.4653 | 2657.2143 | -2916.8975 | 856.9234 | -2916.8975 | 3945.7672 | 0.67343
[6 empty] | 2435779.8134 | -3077735.1262 | 587.8275 | -54674795.4411 | -3077735.1262 | 2435.7798 | -3077.7351 | 850.5933 | -3077.7351 | 3924.9811 | 0.62058
[6 empty] | 2214345.2849 | -3218530.2151 | 583.9249 | -54693572.6771 | -3218530.2151 | 2214.3453 | -3218.5302 | 845.0126 | -3218.5302 | 3906.6945 | 0.56681
[6 empty] | 1992910.7564 | -3341482.1968 | 580.4955 | -54710550.535 | -3341482.1968 | 1992.9108 | -3341.4822 | 840.1085 | -3341.4822 | 3890.655 | 0.51223
[6 empty] | 1771476.228 | -3448254.7486 | 577.5008 | -54725732.3524 | -3448254.7486 | 1771.4762 | -3448.2547 | 835.8261 | -3448.2547 | 3876.6724 | 0.45696
[6 empty] | 1550041.6995 | -3540128.1208 | 574.9115 | -54739121.1067 | -3540128.1208 | 1550.0417 | -3540.1281 | 832.1234 | -3540.1281 | 3864.6004 | 0.40109
[6 empty] | 1328607.171 | -3618097.5438 | 572.7049 | -54750719.4181 | -3618097.5438 | 1328.6072 | -3618.0975 | 828.968 | -3618.0975 | 3854.3257 | 0.34471
[6 empty] | 1107172.6425 | -3682938.9985 | 570.8633 | -54760529.5526 | -3682938.9985 | 1107.1726 | -3682.939 | 826.3345 | -3682.939 | 3845.7601 | 0.28789
[6 empty] | 885738.114 | -3735254.2715 | 569.3731 | -54768553.4235 | -3735254.2715 | 885.7381 | -3735.2543 | 824.2036 | -3735.2543 | 3838.8353 | 0.23073
[6 empty] | 664303.5855 | -3775502.2781 | 568.2241 | -54774792.594 | -3775502.2781 | 664.3036 | -3775.5023 | 822.5604 | -3775.5023 | 3833.4993 | 0.17329
[6 empty] | 442869.057 | -3804020.8893 | 567.4084 | -54779248.2781 | -3804020.8893 | 442.8691 | -3804.0209 | 821.3941 | -3804.0209 | 3829.7138 | 0.11564
[6 empty] | 221434.5285 | -3821041.8901 | 566.9211 | -54781921.3423 | -3821041.8901 | 221.4345 | -3821.0419 | 820.6971 | -3821.0419 | 3827.4527 | 0.057854
[6 empty] | -5.2387e-10 | -3826700.7067 | 566.759 | -54782812.306 | -3826700.7067 | -5.2387e-13 | -3826.7007 | 820.4653 | -3826.7007 | 3826.7007 | -1.369e-16
Note on B22: Autor: P_max no se da con reactiva 0 a la salida, por lo que el PF a la salida no es 1. La potencia es algo mayor que la rated porque la tension en bornas del stack de potencia es tb algo mayor
Note on B25: IF YES = '1' / NO = '0'

## V_1,1pu_DIG (hidden)
Inverter Voltage | 620 |  |  |  |  | P (W) | Q _Ii(VAr) | Vi_need | Q_Vdc (Var) | Q(Var) | P(kW) | Q_Ii(kVAr) | Vdc_min (V) | Q(kVAr) | S(kVA) | cos fi
Voltage operation pu | 1.1 |  |  | P_manual (kW), Q>0 | 3750 | 3750000 | 2858876.5257 | 744.7123 | -509576.5431 | -509576.5431 | 3750 | 2858.8765 | 1074.9386 | -509.5765 | 3784.4641 | 0.99089 | Capacitive
Line-Line Voltage (V) | 682 |  |  | P_manual (kW), Q<0 | 2846 | 2846000 | -2848429.7482 | 607.6436 | -56166700.9044 | -2848429.7482 | 2846 | -2848.4297 | 878.9303 | -2848.4297 | 4026.5703 | 0.70681 | Inductive
Nm: Number of modules | 3 |  |  |  |  | 0 | 4943182.7695 | 788.8548 | -258444.1978 | -258444.1978 | 0 | 4943.1828 | 1138.0624 | -258.4442 | 258.4442 | 0
f(Hz) | 50 | wg(Hz) | 314.1593 |  |  | 221434.5285 | 4937626.9713 | 788.7405 | -261068.6532 | -261068.6532 | 221.4345 | 4937.627 | 1137.8989 | -261.0687 | 342.3304 | 0.64684
Height (m) | 2700 |  |  |  |  | 442869.057 | 4920917.4218 | 788.3964 | -265443.2917 | -265443.2917 | 442.8691 | 4920.9174 | 1137.4068 | -265.4433 | 516.3266 | 0.85773
Temperature Max (ºC) ( TM) | 33 | TM_H_corrected(ºC) | 44.25 |  |  | 664303.5855 | 4892926.04 | 787.8196 | -271568.9333 | -271568.9333 | 664.3036 | 4892.926 | 1136.582 | -271.5689 | 717.6691 | 0.92564
Vdc_min (Tmax) | 951.5 | Vdc_min(sat) | 975.26 |  |  | 885738.114 | 4853433.8254 | 787.0051 | -279446.727 | -279446.727 | 885.7381 | 4853.4338 | 1135.4173 | -279.4467 | 928.7747 | 0.95366
TM_derating | 104.5% |  |  |  |  | 1107172.6425 | 4802122.0219 | 785.9456 | -289078.152 | -289078.152 | 1107.1726 | 4802.122 | 1133.9022 | -289.0782 | 1144.2891 | 0.96756
Vdc_min derating | 113.7% |  |  |  |  | 1328607.171 | 4738558.5752 | 784.6312 | -300465.0189 | -300465.0189 | 1328.6072 | 4738.5586 | 1132.0226 | -300.465 | 1362.1587 | 0.97537
Total derating@ TM | 118.8% |  |  |  |  | 1550041.6995 | 4662178.4669 | 783.0487 | -313609.4716 | -313609.4716 | 1550.0417 | 4662.1785 | 1129.7597 | -313.6095 | 1581.4488 | 0.98014
Temperature Min (ºC) ( Tm) | -5 | Tm_H_corrected(ºC) | 6.25 |  |  | 1771476.228 | 4572255.6638 | 781.1816 | -328513.9894 | -328513.9894 | 1771.4762 | 4572.2557 | 1127.0897 | -328.514 | 1801.6796 | 0.98324
Vdc_max (Tmin) | 1130 | Vdc_max(sat) | 1130 |  |  | 1992910.7564 | 4467863.0791 | 779.0085 | -345181.3888 | -345181.3888 | 1992.9108 | 4467.8631 | 1123.9821 | -345.1814 | 2022.5834 | 0.98533
Tm_derating | 111.6% |  |  |  |  | 2214345.2849 | 4347814.6756 | 776.5019 | -363614.8271 | -363614.8271 | 2214.3453 | 4347.8147 | 1120.3977 | -363.6148 | 2244.0011 | 0.98678
Vdc_derating(V) | 106% |  |  |  |  | 2435779.8134 | 4210579.8437 | 773.6265 | -383817.8046 | -383817.8046 | 2435.7798 | 4210.5798 | 1116.2859 | -383.8178 | 2465.8344 | 0.98781
Total derating@ Tm | 118.3% |  |  |  |  | 2657214.3419 | 4054152.7356 | 770.3359 | -405794.1682 | -405794.1682 | 2657.2143 | 4054.1527 | 1111.5804 | -405.7942 | 2688.021 | 0.98854
[6 empty] | 2878648.8704 | 3875844.4869 | 766.5678 | -429548.1153 | -429548.1153 | 2878.6489 | 3875.8445 | 1106.192 | -429.5481 | 2910.5207 | 0.98905
Derating factor for TM | 118.3% |  |  |  |  | 3100083.3989 | 3671934.7998 | 762.2359 | -455084.1978 | -455084.1978 | 3100.0834 | 3671.9348 | 1099.9973 | -455.0842 | 3133.3079 | 0.9894
[6 empty] | 3321517.9274 | 3437045.7737 | 757.2151 | -482407.3262 | -482407.3262 | 3321.5179 | 3437.0458 | 1092.8175 | -482.4073 | 3356.3668 | 0.98962
Vi_max (V) | 675.007 |  |  |  |  | 3542952.4559 | 3162906.6598 | 751.3128 | -489517.9442 | -489517.9442 | 3542.9525 | 3162.9067 | 1084.3773 | -489.5179 | 3576.6101 | 0.99059
Ii (A) | 1242.32 |  |  |  |  | 3598311.088 | 3086801.0168 | 749.666 | -496740.6665 | -496740.6665 | 3598.3111 | 3086.801 | 1082.0224 | -496.7407 | 3632.4364 | 0.99061
P_max (W) (kW) | 4428690.5699 | P_base (kW) | 4428.6906 |  |  | 3653669.7202 | 3007126.0244 | 747.9381 | -504075.5804 | -504075.5804 | 3653.6697 | 3007.126 | 1079.5515 | -504.0756 | 3688.278 | 0.99062
Prated (W) | 4402503.741 | Prated (kW) | 4402.5037 |  |  | 3709028.3523 | 2923525.6189 | 746.1208 | -511522.7748 | -511522.7748 | 3709.0284 | 2923.5256 | 1076.9527 | -511.5228 | 3744.135 | 0.99062
[6 empty] | 3764386.9844 | 2835573.2747 | 744.204 | -519082.3402 | -519082.3402 | 3764.387 | 2835.5733 | 1074.2117 | -519.0823 | 3800.0073 | 0.99063
GPTech Inverter | 1 |  |  |  |  | 3819745.6165 | 2742750.6714 | 742.1758 | -526754.3682 | -526754.3682 | 3819.7456 | 2742.7507 | 1071.3113 | -526.7544 | 3855.8951 | 0.99062
Inverter output current (A) | 1250 |  |  |  |  | 3875104.2486 | 2644417.2206 | 740.021 | -534538.9522 | -534538.9522 | 3875.1042 | 2644.4172 | 1068.2301 | -534.539 | 3911.7982 | 0.99062
[6 empty] | 3930462.8808 | 2539765.1458 | 737.7209 | -542436.1869 | -542436.1869 | 3930.4629 | 2539.7651 | 1064.9409 | -542.4362 | 3967.7167 | 0.99061
Set Point Calculation Tool (@Tmax) | [5 empty] | 3985821.5129 | 2427750.7236 | 735.251 | -550446.1685 | -550446.1685 | 3985.8215 | 2427.7507 | 1061.409 | -550.4462 | 4023.6506 | 0.9906
P | 2846 | 2846 |  |  |  | 4041180.145 | 2306984.0863 | 732.5788 | -558568.9949 | -558568.9949 | 4041.1801 | 2306.9841 | 1057.5877 | -558.569 | 4079.6 | 0.99058
| Q_ind_lim | -2848.4297 |  |  |  | 4096538.7771 | 2175542.1764 | 729.6593 | -566804.7651 | -566804.7651 | 4096.5388 | 2175.5422 | 1053.4128 | -566.8048 | 4135.565 | 0.99056
| Q_cap_lim | -402.4423 |  |  |  | 4151897.4093 | 2030626.8845 | 726.4269 | -575153.5799 | -575153.5799 | 4151.8974 | 2030.6269 | 1048.7904 | -575.1536 | 4191.5455 | 0.99054
Q | 0 | -402.4423 |  |  |  | 4207256.0414 | 1867874.9265 | 722.7794 | -583615.5414 | -583615.5414 | 4207.256 | 1867.8749 | 1043.5745 | -583.6155 | 4247.5417 | 0.99052
PF | 0.99015 | Io(P,Q) (A) | 2433.2631 |  |  | 4262614.6735 | 1679752.1298 | 718.5402 | -592190.7536 | -592190.7536 | 4262.6147 | 1679.7521 | 1037.5125 | -592.1908 | 4303.5536 | 0.99049
Vdc_min(V) | 961.5 |  |  |  |  | 4317973.3056 | 1450878.1898 | 713.3488 | -600879.3214 | -600879.3214 | 4317.9733 | 1450.8782 | 1030.0888 | -600.8793 | 4359.5813 | 0.99046
Vac_max(V) | 665.3846 |  |  |  |  | 4373331.9378 | 1136944.4757 | 706.166 | -609681.3518 | -609681.3518 | 4373.3319 | 1136.9445 | 1019.8174 | -609.6814 | 4415.6249 | 0.99042
[6 empty] | 4428690.5699 | 527605.0268 | 692.0587 | -600879.3214 | 527605.0268 | 4428.6906 | 527.605 | 999.6439 | 527.605 | 4460.0075 | 0.99298
[6 empty] | 4373331.9378 | -81734.4221 | 677.5613 | -55968263.881 | -81734.4221 | 4373.3319 | -81.7344 | 978.9127 | -81.7344 | 4374.0956 | 0.99983
[6 empty] | 4317973.3056 | -395668.1363 | 669.9949 | -55976952.4488 | -395668.1363 | 4317.9733 | -395.6681 | 968.0927 | -395.6681 | 4336.0635 | 0.99583
[6 empty] | 4262614.6735 | -624542.0762 | 664.4243 | -55985527.6609 | -624542.0762 | 4262.6147 | -624.5421 | 960.1268 | -624.5421 | 4308.1245 | 0.98944
[6 empty] | 4207256.0414 | -812664.8729 | 659.8103 | -55993989.6225 | -812664.8729 | 4207.256 | -812.6649 | 953.5288 | -812.6649 | 4285.0236 | 0.98185
[6 empty] | 4151897.4093 | -975416.8309 | 655.7924 | -56002338.4373 | -975416.8309 | 4151.8974 | -975.4168 | 947.7832 | -975.4168 | 4264.9373 | 0.9735
[6 empty] | 4096538.7771 | -1120332.1229 | 652.194 | -56010574.2075 | -1120332.1229 | 4096.5388 | -1120.3321 | 942.6375 | -1120.3321 | 4246.9723 | 0.96458
[6 empty] | 4041180.145 | -1251774.0327 | 648.9129 | -56018697.0338 | -1251774.0327 | 4041.1801 | -1251.774 | 937.9455 | -1251.774 | 4230.6117 | 0.95522
[6 empty] | 3985821.5129 | -1372540.6701 | 645.8836 | -56026707.0155 | -1372540.6701 | 3985.8215 | -1372.5407 | 933.6136 | -1372.5407 | 4215.5238 | 0.94551
[6 empty] | 3930462.8808 | -1484555.0923 | 643.0611 | -56034604.2502 | -1484555.0923 | 3930.4629 | -1484.5551 | 929.5774 | -1484.5551 | 4201.481 | 0.93549
[6 empty] | 3875104.2486 | -1589207.1671 | 640.4128 | -56042388.8342 | -1589207.1671 | 3875.1042 | -1589.2072 | 925.7904 | -1589.2072 | 4188.3186 | 0.92522
[6 empty] | 3819745.6165 | -1687540.6178 | 637.9145 | -56050060.8622 | -1687540.6178 | 3819.7456 | -1687.5406 | 922.2177 | -1687.5406 | 4175.9131 | 0.91471
[6 empty] | 3764386.9844 | -1780363.2212 | 635.5471 | -56057620.4275 | -1780363.2212 | 3764.387 | -1780.3632 | 918.8324 | -1780.3632 | 4164.1689 | 0.90399
[6 empty] | 3709028.3523 | -1868315.5654 | 633.2958 | -56065067.622 | -1868315.5654 | 3709.0284 | -1868.3156 | 915.613 | -1868.3156 | 4153.0103 | 0.89309
[6 empty] | 3653669.7202 | -1951915.9709 | 631.1484 | -56072402.5359 | -1951915.9709 | 3653.6697 | -1951.916 | 912.5422 | -1951.916 | 4142.3759 | 0.88202
[6 empty] | 3598311.088 | -2031590.9633 | 629.095 | -56079625.2581 | -2031590.9633 | 3598.3111 | -2031.591 | 909.6059 | -2031.591 | 4132.2155 | 0.87079
[6 empty] | 3542952.4559 | -2107696.6062 | 627.1274 | -56086735.8762 | -2107696.6062 | 3542.9525 | -2107.6966 | 906.7922 | -2107.6966 | 4122.4868 | 0.85942
[6 empty] | 3321517.9274 | -2381835.7201 | 619.988 | -56114059.0046 | -2381835.7201 | 3321.5179 | -2381.8357 | 896.5828 | -2381.8357 | 4087.2512 | 0.81265
[6 empty] | 3100083.3989 | -2616724.7463 | 613.8047 | -56139595.0871 | -2616724.7463 | 3100.0834 | -2616.7247 | 887.7407 | -2616.7247 | 4056.8172 | 0.76417
[6 empty] | 2878648.8704 | -2820634.4334 | 608.386 | -56163349.0342 | -2820634.4334 | 2878.6489 | -2820.6344 | 879.9919 | -2820.6344 | 4030.2107 | 0.71427
[6 empty] | 2657214.3419 | -2998942.6821 | 603.6077 | -56185325.3978 | -2998942.6821 | 2657.2143 | -2998.9427 | 873.159 | -2998.9427 | 4006.7999 | 0.66318
[6 empty] | 2435779.8134 | -3155369.7902 | 599.3845 | -56205528.3753 | -3155369.7902 | 2435.7798 | -3155.3698 | 867.1198 | -3155.3698 | 3986.1487 | 0.61106
[6 empty] | 2214345.2849 | -3292604.622 | 595.6547 | -56223961.8135 | -3292604.622 | 2214.3453 | -3292.6046 | 861.7862 | -3292.6046 | 3967.9428 | 0.55806
[6 empty] | 1992910.7564 | -3412653.0255 | 592.3728 | -56240629.213 | -3412653.0255 | 1992.9108 | -3412.653 | 857.0931 | -3412.653 | 3951.9481 | 0.50429
[6 empty] | 1771476.228 | -3517045.6103 | 589.504 | -56255533.7307 | -3517045.6103 | 1771.4762 | -3517.0456 | 852.9907 | -3517.0456 | 3937.9865 | 0.44984
[6 empty] | 1550041.6995 | -3606968.4133 | 587.0216 | -56268678.1835 | -3606968.4133 | 1550.0417 | -3606.9684 | 849.4409 | -3606.9684 | 3925.9203 | 0.39482
[6 empty] | 1328607.171 | -3683348.5217 | 584.9048 | -56280065.0504 | -3683348.5217 | 1328.6072 | -3683.3485 | 846.4139 | -3683.3485 | 3915.6421 | 0.33931
[6 empty] | 1107172.6425 | -3746911.9683 | 583.1374 | -56289696.4754 | -3746911.9683 | 1107.1726 | -3746.912 | 843.8865 | -3746.912 | 3907.068 | 0.28338
[6 empty] | 885738.114 | -3798223.7719 | 581.7067 | -56297574.2691 | -3798223.7719 | 885.7381 | -3798.2238 | 841.8406 | -3798.2238 | 3900.1328 | 0.2271
[6 empty] | 664303.5855 | -3837715.9864 | 580.6032 | -56303699.9107 | -3837715.9864 | 664.3036 | -3837.716 | 840.2625 | -3837.716 | 3894.7867 | 0.17056
[6 empty] | 442869.057 | -3865707.3682 | 579.8197 | -56308074.5492 | -3865707.3682 | 442.8691 | -3865.7074 | 839.1422 | -3865.7074 | 3890.993 | 0.11382
[6 empty] | 221434.5285 | -3882416.9178 | 579.3515 | -56310699.0045 | -3882416.9178 | 221.4345 | -3882.4169 | 838.4727 | -3882.4169 | 3888.7266 | 0.056943
[6 empty] | -5.2387e-10 | -3887972.7159 | 579.1958 | -56311573.7684 | -3887972.7159 | -5.2387e-13 | -3887.9727 | 838.25 | -3887.9727 | 3887.9727 | -1.3474e-16
Note on B22: Autor: P_max no se da con reactiva 0 a la salida, por lo que el PF a la salida no es 1. La potencia es algo mayor que la rated porque la tension en bornas del stack de potencia es tb algo mayor
Note on B25: IF YES = '1' / NO = '0'

## DIGSILENT CAPABILITY TABLES (hidden)
|  |  | Vdc Limited | P/Prated
| Pbase | P (pu) | Qcapacitivo(pu)
0 | 4.0261 | 0 | V/Vrated | 0 | 0.055 | 0.11 | 0.165 | 0.22 | 0.275 | 0.33 | 0.385 | 0.44 | 0.495 | 0.55 | 0.605 | 0.66 | 0.715 | 0.77 | 0.825 | 0.88 | 0.89375 | 0.9075 | 0.92125 | 0.935 | 0.94875 | 0.9625 | 0.97625 | 0.99 | 1.0037 | 1.0175 | 1.0312 | 1.045 | 1.0588 | 1.0725 | 1.0862 | 1.1
1 |  | 0.055 | 0.9 | 0.98506 | 0.98337 | 0.97829 | 0.96976 | 0.95767 | 0.94188 | 0.92218 | 0.89827 | 0.86978 | 0.83618 | 0.79675 | 0.75044 | 0.69568 | 0.62993 | 0.5485 | 0.44069 | 0.26325 | 0.16786 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726
2 |  | 0.11 | 0.92 | 0.90798 | 0.90772 | 0.90694 | 0.90564 | 0.90382 | 0.90148 | 0.89862 | 0.89523 | 0.89133 | 0.86392 | 0.82576 | 0.78114 | 0.72869 | 0.66627 | 0.59016 | 0.49263 | 0.3505 | 0.29808 | 0.22523 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668
3 |  | 0.165 | 0.94 | 0.81856 | 0.81831 | 0.81754 | 0.81627 | 0.81449 | 0.8122 | 0.8094 | 0.80609 | 0.80227 | 0.79793 | 0.79308 | 0.78772 | 0.76111 | 0.70163 | 0.63 | 0.54039 | 0.41815 | 0.37781 | 0.32983 | 0.26796 | 0.16012 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697
4 |  | 0.22 | 0.96 | 0.7245 | 0.72425 | 0.72351 | 0.72226 | 0.72052 | 0.71827 | 0.71553 | 0.71229 | 0.70855 | 0.7043 | 0.69955 | 0.6943 | 0.68855 | 0.68228 | 0.66836 | 0.58512 | 0.47631 | 0.44239 | 0.40411 | 0.35952 | 0.30457 | 0.2264 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812
5 |  | 0.275 | 0.98 | 0.6258 | 0.62555 | 0.62482 | 0.6236 | 0.62189 | 0.6197 | 0.61701 | 0.61384 | 0.61017 | 0.60601 | 0.60136 | 0.59622 | 0.59058 | 0.58444 | 0.57781 | 0.57068 | 0.52866 | 0.4989 | 0.46618 | 0.42962 | 0.38773 | 0.33767 | 0.27228 | 0.14472 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401
6 |  | 0.33 | 1 | 0.52245 | 0.52221 | 0.52149 | 0.5203 | 0.51862 | 0.51647 | 0.51384 | 0.51073 | 0.50713 | 0.50306 | 0.4985 | 0.49346 | 0.48794 | 0.48193 | 0.47543 | 0.46844 | 0.46096 | 0.45902 | 0.45704 | 0.45503 | 0.453 | 0.41483 | 0.36846 | 0.31084 | 0.22657 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083
7 |  | 0.385 | 1.02 | 0.41445 | 0.41422 | 0.41351 | 0.41234 | 0.4107 | 0.40859 | 0.40601 | 0.40296 | 0.39944 | 0.39544 | 0.39098 | 0.38604 | 0.38062 | 0.37473 | 0.36836 | 0.36151 | 0.35419 | 0.35228 | 0.35034 | 0.34837 | 0.34638 | 0.34435 | 0.34229 | 0.3402 | 0.33808 | 0.27618 | 0.11268 | 0.11268 | 0.11268 | 0.11268 | 0.11268 | 0.11268 | 0.11268
8 |  | 0.44 | 1.04 | 0.30181 | 0.30158 | 0.30089 | 0.29974 | 0.29813 | 0.29606 | 0.29353 | 0.29054 | 0.28709 | 0.28317 | 0.27879 | 0.27395 | 0.26864 | 0.26286 | 0.25662 | 0.2499 | 0.24272 | 0.24085 | 0.23895 | 0.23702 | 0.23506 | 0.23307 | 0.23105 | 0.22901 | 0.22693 | 0.22482 | 0.22269 | 0.22544 | 0.11714 | 0.11714 | 0.11714 | 0.11714 | 0.11714
9 |  | 0.495 | 1.06 | 0.18453 | 0.1843 | 0.18363 | 0.1825 | 0.18092 | 0.17889 | 0.17641 | 0.17347 | 0.17008 | 0.16624 | 0.16194 | 0.15719 | 0.15198 | 0.14631 | 0.14019 | 0.1336 | 0.12656 | 0.12472 | 0.12286 | 0.12097 | 0.11905 | 0.1171 | 0.11512 | 0.11311 | 0.11107 | 0.10901 | 0.10691 | 0.10479 | 0.10263 | 0.10045 | 0.098238 | 0.095997 | 0.093726
10 |  | 0.55 | 1.08 | 0.062599 | 0.062378 | 0.061714 | 0.060607 | 0.059057 | 0.057064 | 0.054628 | 0.051747 | 0.048421 | 0.04465 | 0.040434 | 0.03577 | 0.030658 | 0.025097 | 0.019087 | 0.012625 | 0.0057108 | 0.0039114 | 0.0020836 | 0.00022741 | -0.0016572 | -0.0035703 | -0.0055119 | -0.0074819 | -0.0094805 | -0.011508 | -0.013563 | -0.015648 | -0.017761 | -0.019902 | -0.022073 | -0.024272 | -0.0265
11 |  | 0.605 | 1.1 | -0.064192 | -0.064844 | -0.065931 | -0.067452 | -0.069409 | -0.071801 | -0.07463 | -0.077894 | -0.081596 | -0.085736 | -0.090315 | -0.095333 | -0.10079 | -0.10669 | -0.11303 | -0.11982 | -0.12159 | -0.12338 | -0.1252 | -0.12705 | -0.12893 | -0.13084 | -0.13277 | -0.13473 | -0.13672 | -0.13874 | -0.14078 | -0.14286 | -0.14496 | -0.14709 | -0.14925 | -0.15143 | 0.13105
12 |  | 0.66 | Qinductivo(pu) | P/Prated
13 |  | 0.715 | V/Vrated | 0 | 0.055 | 0.11 | 0.165 | 0.22 | 0.275 | 0.33 | 0.385 | 0.44 | 0.495 | 0.55 | 0.605 | 0.66 | 0.715 | 0.77 | 0.825 | 0.88 | 0.89375 | 0.9075 | 0.92125 | 0.935 | 0.94875 | 0.9625 | 0.97625 | 0.99 | 1.0037 | 1.0175 | 1.0312 | 1.045 | 1.0588 | 1.0725 | 1.0862 | 1.1
14 |  | 0.77 | 0.9 | -0.80961 | -0.80792 | -0.80284 | -0.79431 | -0.78222 | -0.76643 | -0.74673 | -0.72282 | -0.69433 | -0.66073 | -0.6213 | -0.57499 | -0.52023 | -0.45448 | -0.37305 | -0.26524 | -0.087804 | 0.0075918 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726
15 |  | 0.825 | 0.92 | -0.82561 | -0.82396 | -0.81899 | -0.81065 | -0.79884 | -0.78342 | -0.76419 | -0.7409 | -0.71319 | -0.68058 | -0.64243 | -0.5978 | -0.54535 | -0.48294 | -0.40683 | -0.30929 | -0.16717 | -0.11474 | -0.041895 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668
16 |  | 0.88 | 0.94 | -0.84152 | -0.8399 | -0.83504 | -0.82688 | -0.81533 | -0.80027 | -0.7815 | -0.75879 | -0.73181 | -0.70014 | -0.66317 | -0.62009 | -0.56972 | -0.51023 | -0.4386 | -0.34899 | -0.22676 | -0.18641 | -0.13844 | -0.076564 | 0.031274 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697
16.25 |  | 0.89375 | 0.96 | -0.85735 | -0.85576 | -0.851 | -0.84302 | -0.83172 | -0.81699 | -0.79866 | -0.7765 | -0.75022 | -0.71941 | -0.68355 | -0.64189 | -0.59341 | -0.53653 | -0.46874 | -0.3855 | -0.27669 | -0.24277 | -0.20448 | -0.1599 | -0.10495 | -0.026774 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812
16.5 |  | 0.9075 | 0.98 | -0.87308 | -0.87153 | -0.86687 | -0.85905 | -0.84799 | -0.83359 | -0.81567 | -0.79404 | -0.76841 | -0.73842 | -0.70359 | -0.66325 | -0.61649 | -0.56194 | -0.4975 | -0.41953 | -0.32063 | -0.29087 | -0.25815 | -0.22159 | -0.1797 | -0.12964 | -0.064256 | 0.063307 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401
16.75 |  | 0.92125 | 1 | -0.88874 | -0.88722 | -0.88265 | -0.87499 | -0.86416 | -0.85006 | -0.83254 | -0.8114 | -0.7864 | -0.75718 | -0.72331 | -0.6842 | -0.63902 | -0.58658 | -0.52509 | -0.45157 | -0.3604 | -0.33362 | -0.30465 | -0.27299 | -0.23791 | -0.19823 | -0.15185 | -0.094238 | -0.0099636 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083
17 |  | 0.935 | 1.02 | -0.9043 | -0.90281 | -0.89833 | -0.89083 | -0.88022 | -0.86641 | -0.84927 | -0.82861 | -0.80419 | -0.7757 | -0.74274 | -0.70477 | -0.66104 | -0.61052 | -0.55166 | -0.48198 | -0.39707 | -0.37256 | -0.34633 | -0.31807 | -0.28735 | -0.25355 | -0.21571 | -0.17225 | -0.12002 | -0.050827 | 0.11268 | 0.11268 | 0.11268 | 0.11268 | 0.11268 | 0.11268 | 0.11268
17.25 |  | 0.94875 | 1.04 | -0.91978 | -0.91832 | -0.91393 | -0.90657 | -0.89617 | -0.88265 | -0.86587 | -0.84566 | -0.8218 | -0.794 | -0.7619 | -0.72499 | -0.68261 | -0.63385 | -0.57734 | -0.51101 | -0.43132 | -0.40861 | -0.3845 | -0.35878 | -0.33117 | -0.30128 | -0.2686 | -0.23235 | -0.19125 | -0.14303 | -0.082605 | 0.008845 | 0.11714 | 0.11714 | 0.11714 | 0.11714 | 0.11714
17.5 |  | 0.9625 | 1.06 | -0.93517 | -0.93374 | -0.92943 | -0.92221 | -0.91202 | -0.89877 | -0.88233 | -0.86255 | -0.83922 | -0.81208 | -0.78078 | -0.74487 | -0.70375 | -0.6566 | -0.60223 | -0.53886 | -0.46359 | -0.44237 | -0.41997 | -0.39624 | -0.37099 | -0.34396 | -0.31483 | -0.28315 | -0.24825 | -0.20913 | -0.16406 | -0.10957 | -0.036207 | 0.12169 | 0.12169 | 0.12169 | 0.093726
17.75 |  | 0.97625 | 1.08 | -0.95048 | -0.94907 | -0.94484 | -0.93776 | -0.92776 | -0.91477 | -0.89866 | -0.8793 | -0.85648 | -0.82996 | -0.79942 | -0.76445 | -0.7245 | -0.67883 | -0.62641 | -0.56569 | -0.49424 | -0.47427 | -0.45328 | -0.43117 | -0.40779 | -0.38297 | -0.35648 | -0.32803 | -0.29724 | -0.26353 | -0.22609 | -0.18356 | -0.13344 | -0.070021 | 0.030164 | 0.12632 | -0.0265
18 |  | 0.99 | 1.1 | -0.9657 | -0.96432 | -0.96017 | -0.95321 | -0.9434 | -0.93066 | -0.91487 | -0.8959 | -0.87357 | -0.84764 | -0.81782 | -0.78373 | -0.74488 | -0.70059 | -0.64994 | -0.5916 | -0.52351 | -0.50461 | -0.48482 | -0.46405 | -0.44221 | -0.41915 | -0.39473 | -0.36873 | -0.34091 | -0.31092 | -0.27827 | -0.24227 | -0.20185 | -0.15512 | -0.098276 | -0.020301 | 0.13105
18.25 |  | 1.0037
18.5 |  | 1.0175 | NO Vdc Limited
18.75 |  | 1.0312 | Qcapacitivo(pu) | P/Prated
19 |  | 1.045 | V/Vrated | 0 | 0.055 | 0.11 | 0.165 | 0.22 | 0.275 | 0.33 | 0.385 | 0.44 | 0.495 | 0.55 | 0.605 | 0.66 | 0.715 | 0.77 | 0.825 | 0.88 | 0.89375 | 0.9075 | 0.92125 | 0.935 | 0.94875 | 0.9625 | 0.97625 | 0.99 | 1.0037 | 1.0175 | 1.0312 | 1.045 | 1.0588 | 1.0725 | 1.0862 | 1.1
19.25 |  | 1.0588 | 0.9 | 0.98506 | 0.98337 | 0.97829 | 0.96976 | 0.95767 | 0.94188 | 0.92218 | 0.89827 | 0.86978 | 0.83618 | 0.79675 | 0.75044 | 0.69568 | 0.62993 | 0.5485 | 0.44069 | 0.26325 | 0.16786 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726
19.5 |  | 1.0725 | 0.92 | 1.0089 | 1.0073 | 1.0023 | 0.99398 | 0.98217 | 0.96675 | 0.94753 | 0.92424 | 0.89653 | 0.86392 | 0.82576 | 0.78114 | 0.72869 | 0.66627 | 0.59016 | 0.49263 | 0.3505 | 0.29808 | 0.22523 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668
19.75 |  | 1.0862 | 0.94 | 1.0329 | 1.0313 | 1.0264 | 1.0183 | 1.0067 | 0.99166 | 0.97289 | 0.95018 | 0.92321 | 0.89153 | 0.85456 | 0.81148 | 0.76111 | 0.70163 | 0.63 | 0.54039 | 0.41815 | 0.37781 | 0.32983 | 0.26796 | 0.16012 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697
20 |  | 1.1 | 0.96 | 1.057 | 1.0554 | 1.0506 | 1.0426 | 1.0313 | 1.0166 | 0.99828 | 0.97613 | 0.94984 | 0.91903 | 0.88317 | 0.84152 | 0.79303 | 0.73615 | 0.66836 | 0.58512 | 0.47631 | 0.44239 | 0.40411 | 0.35952 | 0.30457 | 0.2264 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812
|  |  | 0.98 | 1.0811 | 1.0796 | 1.0749 | 1.0671 | 1.056 | 1.0416 | 1.0237 | 1.0021 | 0.97644 | 0.94645 | 0.91162 | 0.87128 | 0.82451 | 0.76997 | 0.70553 | 0.62756 | 0.52866 | 0.4989 | 0.46618 | 0.42962 | 0.38773 | 0.33767 | 0.27228 | 0.14472 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401
|  |  | 1 | 1.1053 | 1.1038 | 1.0993 | 1.0916 | 1.0808 | 1.0667 | 1.0491 | 1.028 | 1.003 | 0.97379 | 0.93992 | 0.90081 | 0.85562 | 0.80319 | 0.7417 | 0.66818 | 0.57701 | 0.55023 | 0.52126 | 0.4896 | 0.45451 | 0.41483 | 0.36846 | 0.31084 | 0.22657 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083
|  |  | 1.02 | 1.1297 | 1.1282 | 1.1237 | 1.1162 | 1.1056 | 1.0918 | 1.0746 | 1.054 | 1.0295 | 1.0011 | 0.9681 | 0.93013 | 0.8864 | 0.83588 | 0.77702 | 0.70734 | 0.62243 | 0.59792 | 0.57169 | 0.54343 | 0.51271 | 0.4789 | 0.44107 | 0.39761 | 0.34538 | 0.27618 | 0.11268 | 0.11268 | 0.11268 | 0.11268 | 0.11268 | 0.11268 | 0.11268
|  |  | 1.04 | 1.1541 | 1.1526 | 1.1482 | 1.1408 | 1.1305 | 1.1169 | 1.1001 | 1.0799 | 1.0561 | 1.0283 | 0.99618 | 0.95927 | 0.91689 | 0.86813 | 0.81162 | 0.7453 | 0.6656 | 0.64289 | 0.61879 | 0.59306 | 0.56545 | 0.53556 | 0.50288 | 0.46663 | 0.42553 | 0.37731 | 0.31689 | 0.22544 | 0.11714 | 0.11714 | 0.11714 | 0.11714 | 0.11714
|  |  | 1.06 | 1.1786 | 1.1771 | 1.1728 | 1.1656 | 1.1554 | 1.1421 | 1.1257 | 1.1059 | 1.0826 | 1.0555 | 1.0242 | 0.98825 | 0.94713 | 0.89998 | 0.84561 | 0.78224 | 0.70697 | 0.68575 | 0.66335 | 0.63962 | 0.61437 | 0.58734 | 0.55821 | 0.52653 | 0.49163 | 0.45251 | 0.40743 | 0.35295 | 0.27959 | 0.12169 | 0.12169 | 0.12169 | 0.12169
|  |  | 1.08 | 1.2031 | 1.2017 | 1.1975 | 1.1904 | 1.1804 | 1.1674 | 1.1513 | 1.1319 | 1.1091 | 1.0826 | 1.0521 | 1.0171 | 0.97715 | 0.93148 | 0.87906 | 0.81833 | 0.74689 | 0.72692 | 0.70593 | 0.68382 | 0.66044 | 0.63561 | 0.60913 | 0.58068 | 0.54988 | 0.51618 | 0.47874 | 0.43621 | 0.38609 | 0.32267 | 0.22249 | 0.12632 | 0.12632
|  |  | 1.1 | 1.2278 | 1.2264 | 1.2223 | 1.2153 | 1.2055 | 1.1928 | 1.177 | 1.158 | 1.1357 | 1.1097 | 1.0799 | 1.0458 | 1.007 | 0.96268 | 0.91204 | 0.85369 | 0.7856 | 0.7667 | 0.74691 | 0.72615 | 0.7043 | 0.68125 | 0.65682 | 0.63083 | 0.60301 | 0.57301 | 0.54036 | 0.50437 | 0.46394 | 0.41722 | 0.36037 | 0.28239 | 0.13105
|  |  | Qinductivo(pu) | P/Prated
|  |  | V/Vrated | 0 | 0.055 | 0.11 | 0.165 | 0.22 | 0.275 | 0.33 | 0.385 | 0.44 | 0.495 | 0.55 | 0.605 | 0.66 | 0.715 | 0.77 | 0.825 | 0.88 | 0.89375 | 0.9075 | 0.92125 | 0.935 | 0.94875 | 0.9625 | 0.97625 | 0.99 | 1.0037 | 1.0175 | 1.0312 | 1.045 | 1.0588 | 1.0725 | 1.0862 | 1.1
|  |  | 0.9 | -0.80961 | -0.80792 | -0.80284 | -0.79431 | -0.78222 | -0.76643 | -0.74673 | -0.72282 | -0.69433 | -0.66073 | -0.6213 | -0.57499 | -0.52023 | -0.45448 | -0.37305 | -0.26524 | -0.087804 | 0.0075918 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726 | 0.087726
|  |  | 0.92 | -0.82561 | -0.82396 | -0.81899 | -0.81065 | -0.79884 | -0.78342 | -0.76419 | -0.7409 | -0.71319 | -0.68058 | -0.64243 | -0.5978 | -0.54535 | -0.48294 | -0.40683 | -0.30929 | -0.16717 | -0.11474 | -0.041895 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668 | 0.091668
|  |  | 0.94 | -0.84152 | -0.8399 | -0.83504 | -0.82688 | -0.81533 | -0.80027 | -0.7815 | -0.75879 | -0.73181 | -0.70014 | -0.66317 | -0.62009 | -0.56972 | -0.51023 | -0.4386 | -0.34899 | -0.22676 | -0.18641 | -0.13844 | -0.076564 | 0.031274 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697 | 0.095697
|  |  | 0.96 | -0.85735 | -0.85576 | -0.851 | -0.84302 | -0.83172 | -0.81699 | -0.79866 | -0.7765 | -0.75022 | -0.71941 | -0.68355 | -0.64189 | -0.59341 | -0.53653 | -0.46874 | -0.3855 | -0.27669 | -0.24277 | -0.20448 | -0.1599 | -0.10495 | -0.026774 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812 | 0.099812
|  |  | 0.98 | -0.87308 | -0.87153 | -0.86687 | -0.85905 | -0.84799 | -0.83359 | -0.81567 | -0.79404 | -0.76841 | -0.73842 | -0.70359 | -0.66325 | -0.61649 | -0.56194 | -0.4975 | -0.41953 | -0.32063 | -0.29087 | -0.25815 | -0.22159 | -0.1797 | -0.12964 | -0.064256 | 0.063307 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401 | 0.10401
|  |  | 1 | -0.88874 | -0.88722 | -0.88265 | -0.87499 | -0.86416 | -0.85006 | -0.83254 | -0.8114 | -0.7864 | -0.75718 | -0.72331 | -0.6842 | -0.63902 | -0.58658 | -0.52509 | -0.45157 | -0.3604 | -0.33362 | -0.30465 | -0.27299 | -0.23791 | -0.19823 | -0.15185 | -0.094238 | -0.0099636 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083 | 0.1083
|  |  | 1.02 | -0.9043 | -0.90281 | -0.89833 | -0.89083 | -0.88022 | -0.86641 | -0.84927 | -0.82861 | -0.80419 | -0.7757 | -0.74274 | -0.70477 | -0.66104 | -0.61052 | -0.55166 | -0.48198 | -0.39707 | -0.37256 | -0.34633 | -0.31807 | -0.28735 | -0.25355 | -0.21571 | -0.17225 | -0.12002 | -0.050827 | 0.11268 | 0.11268 | 0.11268 | 0.11268 | 0.11268 | 0.11268 | 0.11268
|  |  | 1.04 | -0.91978 | -0.91832 | -0.91393 | -0.90657 | -0.89617 | -0.88265 | -0.86587 | -0.84566 | -0.8218 | -0.794 | -0.7619 | -0.72499 | -0.68261 | -0.63385 | -0.57734 | -0.51101 | -0.43132 | -0.40861 | -0.3845 | -0.35878 | -0.33117 | -0.30128 | -0.2686 | -0.23235 | -0.19125 | -0.14303 | -0.082605 | 0.008845 | 0.11714 | 0.11714 | 0.11714 | 0.11714 | 0.11714
|  |  | 1.06 | -0.93517 | -0.93374 | -0.92943 | -0.92221 | -0.91202 | -0.89877 | -0.88233 | -0.86255 | -0.83922 | -0.81208 | -0.78078 | -0.74487 | -0.70375 | -0.6566 | -0.60223 | -0.53886 | -0.46359 | -0.44237 | -0.41997 | -0.39624 | -0.37099 | -0.34396 | -0.31483 | -0.28315 | -0.24825 | -0.20913 | -0.16406 | -0.10957 | -0.036207 | 0.12169 | 0.12169 | 0.12169 | 0.12169
|  |  | 1.08 | -0.95048 | -0.94907 | -0.94484 | -0.93776 | -0.92776 | -0.91477 | -0.89866 | -0.8793 | -0.85648 | -0.82996 | -0.79942 | -0.76445 | -0.7245 | -0.67883 | -0.62641 | -0.56569 | -0.49424 | -0.47427 | -0.45328 | -0.43117 | -0.40779 | -0.38297 | -0.35648 | -0.32803 | -0.29724 | -0.26353 | -0.22609 | -0.18356 | -0.13344 | -0.070021 | 0.030164 | 0.12632 | 0.12632
|  |  | 1.1 | -0.9657 | -0.96432 | -0.96017 | -0.95321 | -0.9434 | -0.93066 | -0.91487 | -0.8959 | -0.87357 | -0.84764 | -0.81782 | -0.78373 | -0.74488 | -0.70059 | -0.64994 | -0.5916 | -0.52351 | -0.50461 | -0.48482 | -0.46405 | -0.44221 | -0.41915 | -0.39473 | -0.36873 | -0.34091 | -0.31092 | -0.27827 | -0.24227 | -0.20185 | -0.15512 | -0.098276 | -0.020301 | 0.13105
|  |  |  | 68 | [24 empty] | 31 | 30 |  |  |  |  | 37 | 36